## 0.Hypothesis
País | Barbados |  | Network emission factor
exchange rate (BCD/USD) | 2 |  | Barbados EF | 0.000634 | tonCO2/kWh | Discount rate | 6%
exchange rate in use: | 2
% SAVINGS ON LIGHTING BY TYPE |  |  | EEM LIFETIME
Incandescent | 90% |  | EEM1 | LED lighting | 10
Fluorescent lamp | 63% |  | EEM2 | Light automation | 10
Fluorescent tube | 50% |  | EEM3 | AC automation | 10
LED tube | 0% |  | EEM4 | SP adjusment
LED lamp | 0% |  | EEM5 | Smart thermostats | 10
HPI-HPIT | 50% |  | EEM6 | Insulate AC areas | 25
PLL | 50% |  | EEM7 | Split retrofit | 15
PLC | 50% |  | EEM8 | Central AC retrofit | 20
T5 fluorescent tube | 40% |  | EEM9 | Air inlet adjusment | 25
Halogen | 80% |  | EEM10 | Air curtains Cold rooms | 15
halogen projector lamp | 80% |  | EEM11 | Insulation cold rooms | 25
Sodum (HPS) | 50% |  | EEM12 | Freezer replacement | 15
AR111 | 80% |  | EEM13 | VSD Air compr | 10
LED (projector, others) | 0% |  | EEM14 | VSD funs/pumps | 10
|  |  | EEM15 | Pumps replacemente | 20
|  |  | EEM16 | Windows films | 15
|  |  | PV |  | 25
ER1
Meteorological data (daily radiation, temperature) (sheet ER1)
Global loss coefficient (calculated in sheet ER1)
[8 empty] | Exchanger correction factor |  | 1
[8 empty] | Incidence angle modifier |  | 0.96
MCE 12 | [7 empty] | ER2
% Savings per VSD | 25% | [6 empty] | Daily radiation (on ER2 sheet)
[8 empty] | Eficiency | 12%
MCE13
% Savings per temperature rise | 3% | %/ºC
Energy rates
Fuel charge (EC) | 0.5294
Non fuel charge (EC) | 0.43749
Total | 0.96689
VAT | 15%
Total | 1.0325
Note on N26: Federico González Madina: Este factorr es considerado 1 para facilitar los cálculos y el diseño. No suele variar mucho

## 1.Intro
Walk-Through Audits (WTA)
BARBADOS
CONSULTANCY TO PROVIDE ENERGY EFFICIENCY AND RENEWABLE ENERGY TECHNICAL SERVICES
[11 empty] | Building ID |  |  | 123
Building identification
| Name: |  |  |  |  | UWI Roy Marshall Teaching Complex
| Main activity: |  |  | Classrooms and offices
| Secundary activities: |  |  |  |  | Events
Year of Building's operation start:
Comments:
Geographic location of the building:
| Region: |  |  | Saint Michael |  |  |  |  | Locality: | Cave Hill Campus
| Address: |  | Cave Hill Rd | [12 empty] | ARGENTINA
| GPS coordinates |  |  |  | 13.134494°, -59.629236° | [10 empty] | CHILE
General comments:
Building's contact Information:
| Name: |  | Natasha Corbin | [8 empty] | Position:
| Phone: |  | +1 246 2310118 |  |  |  |  | E-mail: | natasha.corbin@cavehill.uwi.edu
[7 empty] | NAME | [5 empty] | DATE
|  | WTA performed by: |  |  |  |  | Federico Goznalez, Alvaro Suttner and Shaquille Craigg | [5 empty] | 4522400%
1

## 2 Building
2. BUILDING CHARACTERISTICS
Required pictures: Front of the building/s, roof detail, windows and openings details. Include in sheet "Checklist pictures"
|  | Building's total surface (plant+wharehouses+offices, etc.): | [8 empty] | 1000 |  |  | m2
|  | Is there any building's plan or diagram? | [7 empty] | No |  | YES/NO
If not, draw a sketch of the building inlcuding the north orientation and describe characteristics
The buildings walls are masonry, while the floors were constructed using reinforced concrete. The roofs were constructed using a combination of flat concrete and pitched permaclad sheeting on steel trusses.
Construction materials
|  | Construction material |  |  |  | Bricks and block |  | If "Other", specify
|  | Total quantity of floors: |  |  |  | 2
|  | Roof material: |  |  |  | Concrete |  | If "Other", specify |  |  |  |  | combination of flat concrete and pitched permaclad sheeting on steel trusses
|  | Roof angle (estimated): |  |  |  | 45º |  | If "Other", specify |  |  |  |  | also flat concrete roof
|  | Windows frame material |  |  |  | aluminium |  | Condition |  |  |  |  | good
Total windows surface (estimated) per direction:
|  |  |  | North | m2 |  | Direct sunlight restrictions? Eaves, sun blocking films, etc
|  |  |  | East | m2 |  | Direct sunlight restrictions? Eaves, sun blocking films, etc
|  |  |  | South | m2 |  | Direct sunlight restrictions? Eaves, sun blocking films, etc
|  |  |  | West | m2 |  | Direct sunlight restrictions? Eaves, sun blocking films, etc
|  | Recommended windows for sunscreens | [13 empty] | No
|  | Zone |  |  | surface (m2) |  |  |  | Orientation |  |  |  | Comments
1
2
3
4
5
6
7
8
Comments:
Comments about the structure, envelope, metal sheets, shadding, windows suncreens
2

## 3.Services
3. PERSONEEL AND PRODUCTION
| 1 | Operation time and personnel occupied | [5 empty] | 2 | Building's ocupation time
[5 empty] | Start time | End time |  |  |  |  | Period
|  | Monday to Friday |  |  | 8 | 21 |  |  |  |  | High demand | Low demand
|  | Saturday |  |  | 8 | 12 |  |  |  | Hours per day | 8 | 5
|  | Sunday | [7 empty] | Days per week | 5 | 1
|  | Personnel occupied | [7 empty] | Weeks per year | 46
| 3 | Main products or/and services:
|  |  |  | TYPE |  |  | Year's Production | Units(1)
Main products
1
2
3
4
5
6
7
8
|  |  |  | SERVICES OFFERED |  |  | Metric employed | Units
1
2
3
4
5
6
7
(1) Indicate the unit employed: ton, m3, m2, liters, n°, etc.
Si
No
Comments:
3
Note on AC6: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: In case there are different demand seasons

## 3.Proceses (hidden)
3. ONLY FOR CASES WITH PROCESSES
| 5 | Brief description of the productive processes involved in stablishment:
Briefly explain the physical and chemical processes to which the raw material is subjected in the plant until the final products are obtained. Refer to processes such as grinding, washing, drying, cooking, fermentation, pressing, concentration, packaging, etc. If possible, include a flow chart with the sequence and treatment followed by the raw material, incorporated inputs, and the products and by-products obtained. In case of using Steam Generators, indicate the use given to the steam (heating, drying, sterilization, etc.). In case of using Other Heat Equipment (hot water boilers, industrial heaters or thermal fluid boilers), indicate the use given to the useful heat (injection, thermal conditioning, etc.). If you have printed material, please attach it.
Yes
No
|  | Is it available any process diagram? | (Yes/No)
3

## 4.Energy 1
4. ELECTRICITY AND FUEL CONSUMPTION
| 6 | Complete the following information from a recent bill: | [22 empty] | Si
|  | (Please provide a copy of the bills for each of the supplies you have and monthly consumption data for at least 12 months) | [22 empty] | No
|  |  |  | Supply |  | Sector supplied (all the instalations, plant, offices, section A, B, C, etc.) |  |  |  |  | Type of supply (mono or triphasic voltage) |  | Contracted Power (kW) |  |  |  |  | Tariff identification |  |  |  | Monthly consumption available? (Yes/No)
1
2
3
|  |  |  | Is there available information of consumption for at least 12 months? (Yes/No) | [16 empty] | (Yes/No)
| 7 | Are there any electricity generator equipment? | [10 empty] | If No: |  |  | Go to 8
[13 empty] | If Yes: |  |  | Complete the following chart
|  | Type of equipment (A) |  |  |  |  | Power |  |  | Equipment's use (C) |  | Fuel |  | Annual consumption |  |  |  |  | Annual use (hours) |  | Age of equipment (years) |  | Efficiency (%) (E)
[7 empty] | Value | Unit(B) | [5 empty] | Value |  |  | Unit(D)
1
2
3
4
(A) Diesel generator, motor, photovoltaic panel, etc.
(B) Indicate the corresponding unit: kW or HP.
(C) Emergency or scheduled.
(D) Indicate the corresponding unit: tons, m3, kg, litres, etc.
(E) Indicate this information only if it has been calculated from measurements and based on the Lower Calorific Value of the fuel.
| 8 | Does the establishment use Natural Gas? | [14 empty] | If No: |  |  | Go to 9
If yes, from a recent bill for each supply, complete the following information:
(Please provide a copy of the Distributor's bill for each of the supplies you have and the monthly consumption data for at least 12 months)
|  |  | Supply |  | Distribution company |  |  |  | Tariff | [5 empty] | Contracted capacity |  |  |  | Is monthly data available?
1
2
3
|  |  |  | Is there available information of consumption for at least 12 months? (Yes/No) | [16 empty] | (Yes/No)
Comments:
4

## 5.Energy 2
5. ELECTRICITY AND FUEL CONSUMPTION | [8 empty] | Si
| 9 | Annual fuel consumption: |  |  | Provide detailed information on purchases of these fuels. Include purchases of at least 1 year, provide dates and amounts. |  |  |  | No
|  |  |  | Fuel | Annual consumption | Measure unit (A) | Alternative unit
|  |  |  | LPG |  | kg
|  |  |  | Querosene |  | liters
|  |  |  | Gasoline |  | liters
|  |  |  | Gasoil |  | liters
|  |  |  | Fueloil |  | tons
|  |  |  | Biomass (firewood) |  | tons
|  |  |  | Firewood quality (mark an X): |  | Green firewood (more than 40% moisture)
Aired firewood (humidity between 30% and 40% moisture)
Dried firewood (less than 30% moiture)
|  |  |  | % chipped firewood |  | %
|  |  |  | % unchipped firewood |  | %
|  |  |  | Otros (especificar): |  | tons
(A) If the unit of measure is different from the one indicated, cross it out and put the correct one to the right.
is there available information of consumption for at least 12 months? (Yes/No)
Comments:
5

## 6.Steam (hidden)
6. PRODUCTION, DISTRIBUTION AND USE OF STEAM
| 11 | Do you use steam generators? | [8 empty] | If No: |  | Go to 13 |  |  |  | Si
No
| Concept | [5 empty] | Unit |  | S.G. 1 | S.G. 2 |  |  |  | S.G. 3
Steam Generator brand and model
| Average real steam production | [5 empty] | kg steam/h
| Steam pressure | [6 empty] | (A)
| Steam temperature(B) | [5 empty] | °C
| Feed water temperature | [5 empty] | °C
| Flue gas chimney temperature (C) | [5 empty] | °C
| Annual use of steam generator |  |  | Hours per day |  |  | Qty
|  |  |  | Time range(s) (D) |  |  | range
|  |  |  | Days per week |  |  | Qty
|  |  |  | Weeks per year |  |  | Qty
| ELECTRICITY OR USED FUELS |  | Electricity or main fuel I |  |  |  | name
|  |  | Alternative fuel II |  |  |  | name
|  |  | Alternative fuel III |  |  |  | name
|  |  | Percentaje of year using I |  |  |  | %
|  |  | Percentaje of year using II |  |  |  | %
|  |  | Percentaje of year using III |  |  |  | %
|  |  | Power or consumption per hour of I |  |  |  |  | (E)
|  |  | Consumption per hour of II |  |  |  |  | (E)
|  |  | Consumption per hour of III |  |  |  |  | (E)
| Rendimiento (Sólo si es medido y referido a PCI) | [5 empty] | %
| STEAM USES |  | Low pressure steam (< 5 kg/cm2) |  |  |  | %
|  |  | Mid pressure steam (5 a 15 kg/cm2) |  |  |  | %
|  |  | High pressure steam (> 15 kg/cm2) |  |  |  | %
|  |  | Total |  |  |  | % |  | 100 | 100 |  |  |  | 100
|  |  | Industrial water heating |  |  |  | %
|  |  | Offices, locker rooms, dining room |  |  |  | %
|  |  | Time range(s) (F) |  |  |  | range
| Percentage of steam produced that is mixed | [5 empty] | %
| Percentage of steam produced that is recovered | [5 empty] | %
Complete only if it's measured total annual steam production or electricity or fuel consumption:
| Annual steam production | [6 empty] | (G)
| Electricity or fuel I annualy consumption | [6 empty] | (G)
| Fuel II annualy consumption | [6 empty] | (G)
| Fuel III annualy consumption | [6 empty] | (G)
Complete only if flue gas measurements are performed:
| Carbon dioxide percentage (CO2) | [5 empty] | %
| Oxigen percentage (O2) | [5 empty] | %
| Carbon monoxide concentration (CO) | [5 empty] | ppm
| Flue gas chimney temperature | [5 empty] | °C
| Combustion efficiency | [5 empty] | %
(A) Indicate the corresponding unit: kg/cm2, bar, atm, psi, etc.
(B) Indicate only in the case of producing SUPERHEATED steam. If the steam is saturated, write "saturation".
(C) Indicate only if it is measured by a thermometer.
(D) If hourly steam consumption is measured, attach a representative graph of a typical day.
(E) Indicate the corresponding unit: kW, kg/h, l/h, m3/h, kcal/h, BTU/h, etc.
(F) If hourly steam consumption for industrial water heating and non-productive uses is measured, attach a graph of a typical day.
(G) Indicate the corresponding unit: tons, m3, etc.
| 12 | Indicate the following data of the steam distribution system:
[5 empty] | Concepto |  |  |  |  | Unit |  | Value |  |  | Outdoor
[5 empty] | Approximate length of steam pipes |  |  |  |  | meters |  |  |  |  | N/A
[5 empty] | State of the insulation of the steam pipes | With insulation |  |  |  | %
[6 empty] | Without insulation |  |  |  | %
[6 empty] | Total |  |  |  | % |  | 100 |  |  | N/A
Comments:
6

## 6.Others heat
6. OTHER HEAT EQUIPMENT
| 13 | Do you use hot water boilers, boilers for productive use, electric boilers or thermal fluid boilers? | [7 empty] | If No: | Si | caldera eléctrica
[11 empty] | No | caldera a gas natural
| Concept |  |  |  | Unit |  | Equipment 1 | Equipment 2 | Equipment 3 | Equipment 4
| Equipment type (A) |  |  |  | specify
| Brand/model |  |  |  | specify
| Number of same equipment |  |  |  | nº
| Heating fluid (B) |  |  |  | specify
| Estimated age |  |  |  | years
| Solar water heater |  |  |  | Yes/No
| Acumulation tank size |  |  |  | lt
| Solar surface |  |  |  | m2
| Rated heat output |  |  |  |  | (C)
| Maximum working pressure |  |  |  |  | (C)
| Work pressure |  |  |  |  | (D)
| Actual Average Fluid Production |  |  |  | kg/hr
| Fluid input temperature |  |  |  | °C
| Fluid output temperature |  |  |  | °C
| Flue gas chimney temperature (E) |  |  |  | °C
| Temperature (average) of chimney wall |  |  |  | °C
| Annual use of equipment |  |  | Hours per day | Qty
|  |  |  | Time range(s) (F) | range
|  |  |  | Days per week | Qty
|  |  |  | Weeks per year | Qty
| ELECTRICITY OR USED FUELS |  | Electricity or main fuel I |  | name
|  |  | Alternative fuel II |  | name
|  |  | Alternative fuel III |  | name
|  |  | Percentaje of year using I |  | %
|  |  | Percentaje of year using II |  | %
|  |  | Percentaje of year using III |  | %
|  |  | Power or consumption per hour of I |  |  | (G)
|  |  | Consumption per hour of II |  |  | (G)
|  |  | Consumption per hour of III |  |  | (G)
| Rendimiento (Sólo si es medido y referido a PCI) |  |  |  | %
| USES OF HEAT |  | Use I |  | specify
|  |  | Use II |  | specify
|  |  | Use III |  | specify
|  |  | Percentage of heat in Use I |  | %
|  |  | Percentage of heat in Use II |  | %
|  |  | Percentage of heat in Use III |  | %
|  |  | Total |  | % |  | 100 | 100 | 100 | 100
Complete only if it's measured total annual electricity or fuel consumption:
| Electricity or fuel I annualy consumption |  |  |  |  | (H)
| Fuel II annualy consumption |  |  |  |  | (H)
| Fuel III annualy consumption |  |  |  |  | (H)
(A) Boiler, water heater, solar heater, etc.
(B) Indicate if water, oil, etc. are heated.
(C) Indicate the corresponding unit: BTU/h, kcal/h, etc.
(D) Indicate the corresponding unit: kg/cm2, bar, atm, psi, etc.
(E) Indicate only if it is measured by a thermometer.
(F) If hourly steam consumption is measured, attach a representative graph of a typical day.
(G) Indicate the corresponding unit: kW, kg/h, l/h, m3/h, kcal/h, BTU/h, etc.
(H) Indicate the corresponding unit: tons, m3, etc.
Comments:

## 8.Direct heat (hidden)
8. DIRECT HEAT (ovens, heaters, dryers, etc.) | [13 empty] | Si
| 16 | Do you use any equipment to produce direct heat? | [8 empty] | If No: | Go to 17 |  | No
(Only equipment with fuel or electricity as a heat source. Group equipment with the same characteristics and use)
| Concept |  |  |  | Unit |  | Equipment 1 | Equipment 2 | Equipment 3 | Equipment 4 |  | Equipment 5
| Equipment type (A) |  |  |  | specify | [9 empty] | horno
| Number of same equipment |  |  |  | n° | [9 empty] | calentador
| Average age |  |  |  | years | [9 empty] | secadero
| Process or application of heat |  |  |  | specify | [9 empty] | otro
| Product obteined |  |  |  | specify
Data per equipment (individual):
| Flue gas chimney temperature |  |  |  | °C
| Average output production |  |  |  | kg product/hr
| Process working temperature |  |  |  | °C
| Annual use of equipment |  |  | Hours per day | Qty
|  |  |  | Days per week | Qty
|  |  |  | Weeks per year | Qty
| ELECTRICITY OR USED FUELS |  | Electricity or main fuel I |  | name
|  |  | Alternative fuel II |  | name
|  |  | Percentaje of year using I |  | %
|  |  | Percentaje of year using II |  | %
|  |  | Power or consumption per hour of I |  |  | (B)
|  |  | Consumption per hour of II |  |  | (B)
| Rendimiento (Sólo si es medido y referido a PCI) |  |  |  | %
| Air recirculation percentage |  |  |  | %
| Does it preheat combustion air? |  |  |  | Yes/No
| Does it recover heat from combustion gases? |  |  |  | Yes/No
| Does it recover heat from the product obtained? |  |  |  | Yes/No
| (A) Furnace, heater, dryer, reactor, etc. |  |  |  | (B) kW, W, l/h, kg/h, m3/h, etc.
Comments:
8

## 9.Heat & engines (hidden)
9. DIRECT HEAT (ovens, heaters, dryers, etc.)
No
[5 empty] | Unit |  | Equipment 1 |  | Equipment 2 |  | Equipment 3 |  | Equipment 4 |  |  | Equipment 5 |  |  | Equipment 6 |  | Equipment 7 |  |  | Equipment 8
Complete only if it's measured total annual electricity or fuel consumption:
| Electricity or fuel I annualy consumption |  |  |  |  | (C)
| Fuel II annualy consumption |  |  |  |  | (C)
| Fuel III annualy consumption |  |  |  |  | (C)
Complete only if the equipment is a dryer
| Input product moisture content |  |  |  | %
| Output product moisture content |  |  |  | %
Complete only if the equipment is a furnace or heater
| Type (batch or continuous) |  |  |  | specify
| Input product temperature |  |  |  | °C
| Equipment surface area |  |  |  | m2
| Equipment openings area |  |  |  | m2
Complete only if flue gas measurements are performed:
| Oxigen percentage (O2) |  |  |  | %
| Flue gas chimney temperature |  |  |  | °C
| Temperature (average) of chimney wall |  |  |  | °C
(C) kWh, tons, m3, etc.
ENGINES
| 17 Do you use thermal machines for fixed engines (internal combustion engines, turbines, etc.)? | [13 empty] | If No: |  | Go to 18
(Group equipment with the same characteristics and use. DO NOT INCLUDE power generation equipment here)
Data per equipment (individual):
|  |  | Machine type (A) | Use or equipment that drives (B) |  | Number of equal equipments |  | Average age (years) |  | Power |  | Fuel (D) |  |  | Consumption per hour |  |  |  | Annual use |  |  |  | Does it recover waste heat?
[10 empty] | Value | Unit (C) |  |  |  | Value |  |  | Unit (E) | Hours/day | Days/week |  | weeks/ year
Equipment 1
Equipment 2
Equipment 3
Equipment 4
|  | (A) Otto engine, diesel engine, steam turbine, gas turbine, steam engine. | [7 empty] | (C) HP, CV, kW, etc. |  |  |  | (E) l/h, kg/h, kcal/h, etc.
|  | (B) Pump, compressor, mill, etc. | [7 empty] | (D) Diesel, gasoline, etc.
Observaciones:
9

## 7.Electrical motors
7.Electrical Driving force
18 | Do they use electrical motors?
| List all electric motors (Group equipment with the same characteristics and use): | [10 empty] | Complete only if measurements are made (D)
| Equipment type (A) | Equipment name | Brand/ Model | Qty (n°) | Rated power |  | Annual use |  |  | Age (years) | Variable Speed Drive | Measured V (V) | Measured I (A) | Measured power (kW) | Measured PF | Comments | Si
[5 empty] | Value | Unit (B) | Hours/ day | Days/ week | weeks/ year | [7 empty] | No
1 | [16 empty] | Tipo
2 | [16 empty] | Compresor
3 | [16 empty] | Bomba
4 | [16 empty] | Ventilador
5 | [16 empty] | Otros
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
(A) Example: conveyor belts, machine tools, presses, mills, etc.
(C) Answer only if you have a consumption meter.
(E) Indicate this value for the 100% load factor.
Comments:

## 11.Refrigeration system (hidden)
11. Refrigeration processes / Cooling rooms
| 19 | Do you use refrigeration equipment in the processes? | [6 empty] | If No: | Go to 20 |  |  | Si
|  | (Group equipment with the same characteristics and use) | [10 empty] | No
|  | Concept |  | Unit |  | System 1 | System 2 | System 3 |  |  | System 4
|  | Equipment type (A) |  | especify
|  | Number of same equipments |  | n°
|  | Average age |  | years
|  | Product to refrigerate |  | especify
Data per equipment (individual):
|  | Refrigerating capacity |  | kW electrico | (B)
|  | Cold temperature |  | °C
|  | Source of energy (C) |  | especify
|  | Equipment power |  |  | (D)
|  | Annual use of equipment | Hours per day (E) | Qty
|  |  | Days per week | Qty
|  |  | Weeks per year | Qty
|  | Coefficient of performance (C.O.P.) |  | value
Complete only if it's measured total annual energy consumption:
|  | Annual energy consumption |  |  | (F)
Complete only if it is a cold compression equipment:
|  | Motor speed |  | RPM
|  | Average number of rewindings |  | n°
|  | Average load |  | %
|  | Compressor inlet pressure |  |  | (G)
|  | Compressor output pressure |  |  | (G)
(A) Reciprocating compressor, rotary compressor, centrifugal compressor, single or double effect absorption, rooftop, split, chiller.
(B) Indicate the unit: ton of refrigeration/h, frigories/h, BTU/h, etc.
(C) Indicate electricity or fuel used.
(D) Indicate the unit: kW, HP, CV, BTU/h, kcal/h, etc.
(E) They are the hours of cold that can be 24 per day
(F) If it is electricity in kWh; if it is fuel in liters, m3, ton, etc.
(G) Indicate the unit: kg/cm2, bar, atm, psi, etc.
Comments:
12

## 12.Internal transportation (hidden)
12.INTERNAL TRANSPORTATION
| 20 | Do you use vehicles to move loads within the establishment? | [9 empty] | If No: | Go to 21 |  | Si
|  | Example: forklifts, tractors, mobile cranes, etc. DO NOT INCLUDE vehicles leaving the establishment such as cars, vans, trucks, etc. | [12 empty] | No
|  | Type of vehicle |  | Qty (n°) | Rated power |  | Source of energy (B) | Annual use |  |  | Age (years) |  | LPG tank (C)
[5 empty] | Value | Unit (A) |  | hours/day | days/ week | weeks/ year
1
2
3
4
5
6
(A) HP or kW.
(B) Indicate electricity or fuel used. If it is electricity, indicate the number of motor rewindings in Observations.
(C) If they use LPG as a source, indicate: 13 kg LPG tank, gas cylinder, etc.
Comments:
Electricidad
Gas oil
GLP
12

## 8.AC
8. AIR CONDITIONERS
Indicate the artifacts used in offices, dining room, changing rooms, etc.:
|  |  | Indicate air conditioning equipment and other general equipment. | [14 empty] | Yes
|  | Zone | System (a) | Type | Brand/model | Temperature (ºC) | Temp of set point (ºC) | Device's qty (n°) | Thermal power |  | Electrical pwoer |  | COP (B) | Annual use |  |  | Comments
[9 empty] | Value | Unit (C) | Value | Unit (C) |  | hours/day | days/ week | weeks/ year
| 1 | Seminar room | AC | Split | Classic |  | 21 | 1 | 25000 | BTU/h | 2.31 | kW | 3.18 | 8 | 6 | 46
| 2 | Seminar room 2 | AC | Split | Classic |  | 21 | 1 | 25000 | BTU/h | 2.31 | kW | 3.18 | 8 | 6 | 46
| 3 | Seminar room 3 | AC | Split | Daikin |  | 21 | 1 | 24000 | BTU/h | 2.01 | kW | 3.21 | 8 | 6 | 46
| 4 | Computer Lab | AC | Split | MDV |  | 24 | 1 | 21000 | BTU/h | 2.05 | kW | 3 | 8 | 6 | 46
| 5 | Computer Lab | AC | Split | Delta |  | 25 | 1 | 24000 | BTU/h | 2.18 | kW | 3.23 | 8 | 6 | 46
| 6 | Computer Lab | AC | Split | Westinghouse |  | 24 | 1 | 18000 | BTU/h | 1.89 | kW | 2.79 | 8 | 6 | 46
| 7 | Lecture Room | AC | Split | Lennox |  | 24 | 1 | 24000 | BTU/h | 2.43 | kW | 2.89 | 8 | 6 | 46
| 8 | Lecture Room | AC | Split | Midea |  | 23 | 1 | 24000 | BTU/h | 2.43 | kW | 2.93 | 8 | 6 | 46
| 9 | Lecture room Nr2 | AC | Split | Midea |  | 23 | 2 | 24000 | BTU/h | 2.43 | kW | 2.93 | 8 | 6 | 46
| 10 | Lecture room nNr3 | AC | Split | Daikin |  | 25 | 2 | 24000 | BTU/h | 2.01 | kW | 3.21 | 8 | 6 | 46
| 11 | Lecture room nNr3 | AC | Split | MDV |  | 24 | 1 | 21000 | BTU/h | 2.05 | kW | 3 | 8 | 6 | 46
| 12 | Lecture room nNr3 | AC | Split | Streamline |  | 24 | 1 | 24000 | BTU/h | 2.9 | kW | 2.43 | 8 | 6 | 46
| 13 | Lecture Room Nr4 | AC | Split | TCL |  | 24 | 3 | 24000 | BTU/h | 2.175 | kW | 3.23 | 8 | 6 | 46
| 14 | Lecture Room Nr4 | AC | Split | Midea |  | 24 | 1 | 24000 | BTU/h | 2.43 | kW | 2.93 | 8 | 6 | 46
| 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier |  |  | 1 | 43.6992 | kW | 14.5664 | kW | 3 | 8 | 6 | 46
| 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey |  |  | 2 | 69.5258 | kW | 23.1753 | kW | 3 | 8 | 6 | 46
| 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier |  |  | 1 | 43.6992 | kW | 14.5664 | kW | 3 | 8 | 6 | 46
| 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey |  |  | 2 |  |  | 3.725 | kW |  | 8 | 6 | 46
| 19 | Theatre Nr1 | Central AC | Air handler |  |  |  | 1 |  |  | 3.725 | kW |  | 8 | 6 | 46
| 20 | Theatre Nr2 | Central AC | Air handler |  |  |  | 1 |  |  | 3.725 | kW |  | 8 | 6 | 46
| 21 | [8 empty] | kW |  | BTU/h
| 22 | [8 empty] | kW |  | BTU/h
| 23 | [8 empty] | kW |  | BTU/h
| 24 | [8 empty] | kW |  | BTU/h
| 25 | [8 empty] | kW |  | BTU/h
| 26 | [8 empty] | kW |  | BTU/h
| 27 | [8 empty] | kW |  | BTU/h
| 28 | [8 empty] | kW |  | BTU/h
| 29 | [8 empty] | kW |  | BTU/h
| 30 | [8 empty] | kW |  | BTU/h
| 31 | [8 empty] | kW |  | BTU/h
| 32 | [8 empty] | kW |  | BTU/h
| 33 | [8 empty] | kW |  | BTU/h
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
(A) AC for split standard units or Central AC
(B) Indicate or calculate COP
(C) Watt, kW, HP, kcal/h, etc.
Comments:
Note on O28: Federico González: EER

## 9.Lighting
9. LIGHTING | [12 empty] | Type | Wattage | Yes
[6 empty] | If Yes: | Indicate the energy consumed: | [5 empty] | Incandescent | Add mannually | No
[13 empty] | Fluorescent lamp | Add mannually
[13 empty] | Fluorescente tube | 36
| Indicate the data on lighting according to the sectors of the establishment: | [11 empty] | Fluorescente tube short | 18
| (Group the lamps by type and power) | [11 empty] | LED tube | 18
|  | Sector/Area | Luminary Qty (n°) | Lamps Qty (nº) | Type | Control auto? | Rated power (W) | Annual use |  |  | Comments |  | LED tube short | 9
[8 empty] | hours/day | days/ week | weeks/ year |  |  | LED lamp | Add mannually
| 1 | Lobby | 6 | 1 | Fluorescent lamp |  | 15 | 6 | 6 | 46 |  |  | HPI-HPIT | Add mannually
| 2 | Seminar roomx3 | 36 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | PLL | Add mannually
| 3 | Bathroom x 4 | 20 | 1 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | PLC | Add mannually
| 4 | Computer Lab | 32 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | T5 fluorescent tube | 28
| 5 | Storage x 2 | 4 | 2 | Fluorescente tube |  | 36 | 2 | 6 | 46 |  |  | T12 fluorscent tube | 40
| 6 | Hallway | 2 | 1 | LED lamp |  | 10 | 6 | 6 | 46 |  |  | Halogen | Add mannually
| 7 | Hallway | 3 | 1 | Fluorescent lamp |  | 15 | 6 | 6 | 46 |  |  | halogen projector lamp | Add mannually
| 8 | Staff room | 4 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | Sodum (HPS) | Add mannually
| 9 | Lecture Room | 12 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | AR111 | Add mannually
| 10 | Lecture Room | 2 | 1 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | LED (projector, otros) | Add mannually
| 11 | Lecture room Nr2 | 24 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46 |  |  | Other | Add mannually
| 12 | Lecture room Nr2 | 2 | 1 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 13 | Cafeteria | 6 | 2 | Fluorescente tube |  | 36 | 0 | 0 | 0
| 14 | Lecture room nNr3 | 20 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 15 | Lecture room nNr3 | 2 | 1 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 16 | Lecture Room Nr4 | 20 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 17 | Lecture Room Nr4 | 2 | 1 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 18 | Theatre Nr2 | 36 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 19 | Theatre Nr1 | 64 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 20 | Theatre Nr1 | 8 | 1 | Fluorescent lamp |  | 15 | 6 | 6 | 46
| 21 | Theatre Nr3 | 36 | 2 | Fluorescente tube |  | 36 | 6 | 6 | 46
| 22 | Exterior | 8 | 1 | Fluorescent lamp |  | 15 | 12 | 7 | 52
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
(A) Indicate if the indicated consumption corresponds to all the switchboards or to which switchboards in particular.
(B)Halogen, Incandescent, Fluorescent and IM, Mercury Vapor, Metal Halides, High Pressure Sodium, Low Pressure Sodium, LED.
9

## 10. Refrigeration
10. FRIDGES,FREEZERS, COOLING CHAMBER, ICE MACHINES
Yes
No
|  | Zone | System | Type | Brand/model | Temperature (ºC) | Temp Set point (ºC) | Device's qty (n°) | Electric power |  | Thermal pwoer |  | COP | Annual use |  |  | Comments | Lists
[9 empty] | Value | Unit (C) | Value | Unit (C) |  | hours/day | days/ week | weeks/ year
| 1 | Office | Fridges | Small |  | 5 | 7 | 1 | 0.3 | kW |  |  |  | 24 | 7 | 52 |  | Freezer
| 2 | Store room | Freezer | Horizontal 2 door freezer |  |  |  | 3 | 0.5 | kW |  |  |  | 24 | 7 | 52 |  | Fridges
| 3 | [16 empty] | Cold Chamber
| 4 | [16 empty] | Ice Machines
| 5 | [16 empty] | Other
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
(A) Stoves, hot water tanks, water heaters, air conditioners, refrigerators, kitchens, coffee machines, computers, ceiling fan, standing fans, etc.
(B) Electricity, LPG, natural gas, diesel, etc.
(C) Watt, kW, HP, kcal/h, etc.
Comments:
10
Note on K27: Federico González: 300W de evaporadores

## 11. Equipment
11. OTHERS EQUIPMENTS
Indicate the main artifacts you use in offices, dining room, changing rooms, etc.:
|  |  | Indicate air conditioning equipment and other general equipment. | [9 empty] | Yes
No
|  | Zone | Type of device (A) | Model | Device's qty (n°) | Unit power |  | Annual use |  |  | Comments
[6 empty] | Value | Unit (B) | hours/day | days/ week | weeks/ year
| 1 | Lobby | TV | 32" | 1 | 100 |  | 12 | 6 | 46
| 2 | Lobby | Fan |  | 1 | 100 |  | 6 | 6 | 46
| 3 | Seminar rooms | Projector | EPSON | 3 | 300 | W | 6 | 6 | 46
| 4 | Computer LAB | PC |  | 40 | 50 |  | 4 | 6 | 46
| 5 | Computer LAB | Printer |  | 3 | 100 |  | 1 | 6 | 46
| 6 | Lecture rooms | Projector | EPSON | 4 | 300 | W | 6 | 6 | 46
| 7 | Theatres | Projector | EPSON | 3 | 300 | W | 6 | 6 | 46
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
(A) Electric stoves, coffee machines, computers, microwaves, water coolers, electric water heaters, etc.
(B) Watt, kW, HP, kcal/h, etc.
XII. SOLAR POWER
| 27 |  | Do you use solar energy in the establishment? | [7 empty] | If No:
(Identify in Observations those equipments that are not operational)
[6 empty] | Storage tank capacity (l) | Heating temperature (°C) | Energy generation (kcal/year)(A)
Last year's energy generation (kWh/año)
| 28 |  | Are you interested in the use of solar energy in the establishment?
| 29 |  | Have you carried out any technical-economic feasibility study to use solar energy?
Comments:
11

## 12.Compressed air
12. COMPRESSED AIR
Is there a compressed air system?
|  | Name | Use | Compressor type | Age | Brand | Model | Rated power (A) |  | Set point pressure (B) |  | Annual use |  |  | % time loading | % time unloading | Loading power (kW) | Unloading power (kW) | VSD available?
[8 empty] | Value | Unit | Value | Unit | hours/day | days/ week | weeks/ year
Yes
No
[20 empty] | Tipo | Mes | 2022
[8 empty] | (A) kW or HP. | [11 empty] | Positive displacement | Jan | 2021
|  | Brand | Rated power (A) | Annual use |  |  | Measured power (kW)
|  |  |  | hours/day | days/ week | weeks/ year
Dryer 1
Dryer 2
Operation description:

## 13. Pump & vent
13. PUMPING AND VENTILATION
Is there pumping equipment?
| List all the pumping equipment (Group equipment with the same characteristics and use): | [12 empty] | Complete only if measurements are made (E)
| Equipment name | Brand/ Model | Zone/Use | Type of pump/fan (A) | Qty (n°) | Rated power |  | Annual use |  |  | Age (years) | Drive's class (C) | VSD available? | Measured V (V) | Measured I (A) | Measured power (kW) | Measured PF | Comments | Yes
[6 empty] | Value | Unit (B) | Hours/ day | Days/ week | weeks/ year | [8 empty] | No
1 | Pump | Lowara | potable water | pump | 2 | 1.5 | kW | 24 | 7 | 52 | [8 empty] | Tipo
2 | [18 empty] | Compresor
3 | [18 empty] | Bomba
4 | [18 empty] | Ventilador
5 | [18 empty] | Otros
6
7 | [18 empty] | Centrifugue
8 | [18 empty] | Multi-stage submersible
Screw
Is there ventilation equipment?
| List all the ventilation equipment (Group equipment with the same characteristics and use): | [12 empty] | Complete only if measurements are made (E)
| Equipment name | Brand/ Model | Zone/Use | Type of pump/fan (A) | Qty (n°) | Rated power |  | Annual use |  |  | Age (years) | Drive's class (C) | VSD available? | Measured V (V) | Measured I (A) | Measured power (kW) | Measured PF | Comments
[6 empty] | Value | Unit (B) | Hours/ day | Days/ week | weeks/ year
1
2
3
4
5
6
7
8
9
10
(A) (A) Centrifugal, multi-stage submersible, axial, lobe, screw
(B) kW or HP
(C) IE1, IE2, IE3
(D) Answer only if you have a consumption meter.
(E) Measurements made to a motor with the same characteristics
Comments:

## 14.Measurements
14. ON-SITE MEASUREMENTS
| 33 | Power quality measurements or records
|  |  |  | Are there energy quality studies? | [8 empty] | If yes, attach. |  |  |  |  | Yes
No
|  |  | Supply |  | Power (kW) |  |  | Reactive power (kVAr) |  |  | Power factor
1
2
3
| 34 | Measurements of electrical equipment:
|  | Equipment's type |  |  |  | Equipment ID | Voltage (V) | Mono or triphasic |  | Current (A) |  | Power (kW) |  | Reactive power (kVAr) | Power factor
1
2
3
4
5
6
7
8
9
10
11
12
| 35 | Lighting and temperature measurements
|  | Area |  |  |  | Zone | Location | Value (lux) | Temp (°C) | Description (desk, work table, height, etc) |  |  |  |  | Main light source | Secondary light source
1
2
3
4
5
6
7
8
9
10
11
12
| 36 | Thermal equipment
|  | Equipment |  |  |  | Part |  | Value (°C) |  | Thermography description
1
2
3
4
5
6
| 37 | Physical spaces
|  | Places or equipment measured |  |  |  | Description
1
2
3
4
5
6
7
8
18

## List AC
BTU/h a KW
Nr | Denomination | Brand | Model | Brand/model | Unit | Inverter | Type | Thermal Power (BTU/h) | Thermal Power (kW) | Electrical Power (kW) | COP | EER (W/W) | EER (BTU/h/W) | SEER (W/W) | SEER (BTU/h/W) | Comments | 0.0002931
|  | ACSON |  | ACSON - 20470 - |  |  | Split | 20470 | 6 | 1.87 | 3.2086 |  |  |  |  | year 2019
|  | ACSON | A5LC25CJ-ACPOE-R | ACSON - 20000 - A5LC25CJ-ACPOE-R |  |  | Split | 20000 |  | 1.798 | [5 empty] | year 2019 |  | AC | Split
|  | ACSON | A5LCY15F-ACDOA-R | ACSON - 12000 - A5LCY15F-ACDOA-R |  |  | Split | 12000 | 3.5172 | 0.928 | 3.7901 |  |  |  |  | Year 2013 |  | Central AC | Outdoor unit
|  | ACSON | A5WM15G-ACIBE-R | ACSON - 12000 - A5WM15G-ACIBE-R |  | No | Split | 12000 | 3.52 | 1.23 | 2.8618 |  |  |  |  | R410- Year 2009 |  | VRF | Air handler
|  | ACSON | A5WM311-AFCE-R | ACSON - 25997.9529170931 - A5WM311-AFCE-R |  |  | Split | 25997.9529 | 7.62 | 2.56 | 2.9766 |  |  |  |  | Year 2009 |  |  | Cassette
|  | ACSON | ASWM | ACSON - 18000 - ASWM |  |  | Split | 18000 | 5.2758 | 1.88 | 2.8063 |  |  |  |  | Year 2015 |  |  | Heat pump
|  | ACSON | AWM10F-AFAH | ACSON - 9700 - AWM10F-AFAH |  | No | Split | 9700 | 2.843 | 1.037 | 2.7416 |  |  |  |  | R22
|  | ACSON | AWM20F-AFAF | ACSON - 19000 - AWM20F-AFAF | Indoor |  | Split | 19000 | 7.62 | 2.211 | 3.4464 |  |  |  |  | Year 2009
|  | ACSON | AWM20G2 | ACSON - 19003.7529853292 - AWM20G2 |  | No | Split | 19003.753 | 5.57 | 1.807 | 3.0825 |  |  |  |  | R22- Year 2010
|  | AIR CON | ASRCI4H4S37 | AIR CON - 36000 - ASRCI4H4S37 |  |  | Split | 36000 | 10.5516 |  | 3.807 | 3.807 | 12.9888 | 4.8068 | 16.4
|  | AUX | ASW-18B4/EA | AUX - 18000 - ASW-18B4/EA |  |  | Split | 18000 | 5.3 | 2.08 | 2.5481 |  |  |  |  | year 2009
|  | Carrier | 38ARD014.-K903 | Carrier - - 38ARD014.-K903
|  | Carrier | 38AUDA24A0A5A0A0A0 | Carrier - - 38AUDA24A0A5A0A0A0
|  | Carrier | 38QUA048DS | Carrier - - 38QUA048DS | Outdoor
|  | Carrier | 39LD10AA-BA-2NR-19 | Carrier - - 39LD10AA-BA-2NR-19
|  | Carrier | 42CVUR010 | Carrier - 9000 - 42CVUR010 | Indoor | Yes | Split | 9000 | 2.5 | 0.77 | 3.2468
|  | Carrier | 42CVUR013 | Carrier - 12000 - 42CVUR013 | Indoor | Yes | Split | 12000 | 3.5 | 1.09 | 3.211
|  | Carrier | 42CVUR018 | Carrier - 18000 - 42CVUR018 | Indoor | Yes | Split | 18000 | 5 | 1.51 | 3.3113
|  | Carrier | 42CVUR022 | Carrier - 22000 - 42CVUR022 | Indoor | Yes | Split | 22000 | 5.8 | 1.795 | 3.2312
|  | Carrier | 42K060… | Carrier - 12000 - 42K060… | Indoor | No | Split | 12000 | 3.5172 | 1.28 | 2.7478 | 2.7478 |  |  |  | Old
|  | Carrier | 42K64… | Carrier - 9000 - 42K64… | Indoor | No | Split | 9000 | 2.6379 | 0.96 | 2.7478 | 2.7478 |  |  |  | Old
|  | Carrier | 42KHA018L | Carrier - 18000 - 42KHA018L | Indoor |  | Split | 18000 | 5.2758 | 1.83 | 2.883
|  | Carrier | 42KPA009703 | Carrier - 9000 - 42KPA009703 | Indoor | No | Split | 9000 | 2.6379 | 0.95 | 2.7767 | 2.7767 |  |  |  | Old
|  | Carrier | 42QHC018DSW | Carrier - - 42QHC018DSW | Indoor
|  | Carrier | 42QZL024D8S | Carrier - 24000 - 42QZL024D8S | Indoor |  | Ceiling and floor | 24000 | 7.2 |  | 3.9
|  | Carrier | MODEL40RM-012-H913ED | Carrier - - MODEL40RM-012-H913ED
|  | Carrier | TGL-2060CC | Carrier - 36000 - TGL-2060CC |  | No | Split | 36000 | 10.5516 | 3.64 | 2.8988 | 2.8988 |  |  |  | Old
|  | Carrier Xpower | 38VF022H11B016 | Carrier Xpower - - 38VF022H11B016 |  | yes | Heat Pump |  | 61.5
|  | Classic | MRHAEC24DS | Classic - 25000 - MRHAEC24DS | Outdoor | Yes | Split | 25000 | 7.3275 | 2.306 | 3.1776 | 3.05 |  |  |  | 2018
|  | Classic | MW AEC18 | Classic - 18000 - MW AEC18 | Indoor | Yes | Split | 18000 | 5.2758 | 1.645 | 3.2072
|  | Classic | MW FFC 12 (F series) | Classic - 11000 - MW FFC 12 (F series) | Indoor | No | Split | 11000 | 3.2241 | 1.0044 | 3.21 | 3.21
|  | Classic | MW FFC 18S (F series) | Classic - 18000 - MW FFC 18S (F series) | Indoor | No | Split | 18000 | 5.2758 | 1.8577 | 2.84 | 2.84
|  | Classic | MW FFC 24S (F series) | Classic - 22000 - MW FFC 24S (F series) | Indoor | No | Split | 22000 | 6.4482 | 2.2947 | 2.81 | 2.81
|  | ConfortStar | CPE12CD | ConfortStar - 12000 - CPE12CD |  | Yes | Split | 12000 | 3.5172 | 1.11 | 3.1686
|  | ConfortStar | CPE18CD | ConfortStar - 18000 - CPE18CD |  | Yes | Split | 18000 | 5.2758 | 1.718 | 3.0709
|  | Daikin | FTKS09RL215 | Daikin - 9000 - FTKS09RL215 |  | Yes | Split | 9000 | 2.6379 | 0.73072 | 3.61 | 3.21
|  | Daikin | FTKS12RL215 | Daikin - 12000 - FTKS12RL215 |  | Yes | Split | 12000 | 3.5172 | 0.9716 | 3.62 | 3.21
|  | Daikin | FTKS18RL215 | Daikin - 18000 - FTKS18RL215 |  | Yes | Split | 18000 | 5.2758 | 1.4988 | 3.52 | 3.21
|  | Daikin | FTKS24RL215 | Daikin - 24000 - FTKS24RL215 |  | Yes | Split | 24000 | 7.0344 | 1.9984 | 3.52 | 3.21
|  | Daikin | RKS12RL215 | Daikin - 12000 - RKS12RL215 |  | Yes | Split | 12000 | 3.5172 | 1.09 | 3.2268
|  | Daikin | RKS24RL215 | Daikin - 24000 - RKS24RL215 |  | Yes | Split | 24000 | 6.45 | 2.01 | 3.209 | 3.21
|  | Delta | 21WS012C74 | Delta - 12000 - 21WS012C74 |  |  | Split | 12000 | 3.224 | [6 empty] | year 2017
|  | Delta | 26WB024124-070DWFXZ | Delta - 24000 - 26WB024124-070DWFXZ |  |  | Split | 24000 | 7.0344 | 2.18 | 3.2268 |  |  |  |  | year 2016
|  | Delta | 31HF018C74 | Delta - 18000 - 31HF018C74 | Outdoor |  | Split | 18000 | 5.2758 | 1.62 | 3.2567
|  | Delta | 31HF024C74 | Delta - 24000 - 31HF024C74 |  |  | Split | 24000 | 7.0344 | 2.12 | 3.3181
|  | Delta | 35HB012124 | Delta - 12000 - 35HB012124 | Outdoor |  | Split | 12000 | 3.5172 | 1.08 | 3.2567 |  |  |  |  | Year 2016
|  | Delta | 35HG01217 | Delta - 12000 - 35HG01217 |  |  | Split | 12000 | 3.5172 | 2.12 | 1.6591 |  |  |  |  | year 2018
|  | Everwell | ME2433-CU | Everwell - 18000 - ME2433-CU | Outdoor | Yes | Split | 18000 | 5.275 | 1.4632 | 3.6051 | 3.6051 | 12.3 | 3.6051 | 15
|  | Everwell | MG1833 | Everwell - 18000 - MG1833 |  | Yes | Split | 18000 | 5.2758 | 1.8 | 2.931 | 3.6051 | 12.3 | 3.6051 | 15 | year 2016
|  | Everwell | MGCS1233 | Everwell - 12000 - MGCS1233 |  | Yes | Split | 12000 | 3.5172 | 0.97561 | 3.6051 | 3.6051 | 12.3 | 3.6051 | 15
|  | Everwell | MGCS1833 | Everwell - 18000 - MGCS1833 |  | Yes | Split | 18000 | 5.275 | 1.4632 | 3.6051 | 3.6051 | 12.3 | 3.6051 | 15
|  | Frigidaire | FSC24CM5J/FSE24CM5J | Frigidaire - 24000 - FSC24CM5J/FSE24CM5J | indoor |  | split | 24000 | 7.0344 | 2.73 | 2.5767
|  | GREE | GWC12AFC-D3DNA1A/0 | GREE - 12000 - GWC12AFC-D3DNA1A/0 |  | yes | Split | 12000 | 3.5172 |  | 3.2241 | 3.2241 | 11 | 5.862 | 20
|  | GREE | VIR36AC230V1BO | GREE - 33600 - VIR36AC230V1BO |  |  | Split | 33600 | 9.8482 | 4.3 | 2.2903 | 2.4034 | 8.2 | 5.2758 | 18 | Year 2022
|  | Inventor | U7RS-18 | Inventor - 17000 - U7RS-18 |  |  | Cassette | 17000 | 4.9827 | 1.5 | 3.3218 |  |  | 6.7 | 22.8591 | Outdoor
|  | Inventor OMNIA | O1MV1-12 | Inventor OMNIA - 12000 - O1MV1-12 |  |  | Split | 12000 | 3.5172 | 1.58 | 2.2261 |  |  |  |  | R410A
|  | Inventor OMNIA Eco | O3MVI32-12WiFiR | Inventor OMNIA Eco - 12000 - O3MVI32-12WiFiR |  |  | Split | 12000 | 3.5172 |  | 3.61 |  |  |  |  | year 2019-2020
|  | Inventor OMNIA Eco | O3MVI32-24WiFiR | Inventor OMNIA Eco - 24000 - O3MVI32-24WiFiR |  |  | Split | 24000 | 7.0344 |  | 3.61 |  |  |  |  | year 2019-2020
|  | Inventor OMNIA Plus | O2MV1-12WiFiR | Inventor OMNIA Plus - 12000 - O2MV1-12WiFiR |  |  | Split | 12000 | 3.5172 |  | 3.61
|  | Inventor OMNIA Plus | O3MVI32-12WiFiR | Inventor OMNIA Plus - 12000 - O3MVI32-12WiFiR |  |  | Split | 12000 | 3.5172 |  | 3.61 |  |  |  |  | year 2019-2020
5 | Kanion I 9 | Kanion | KWSM-09R410AHS16MV | Kanion - 9000 - KWSM-09R410AHS16MV |  | Yes | Split | 9000 | 2.6379 | 0.68331 | 3.8605 | 3.8605 | 13.1712 | 4.9241 | 16.8
|  | Kanion | KWSM-12IR410ACF | Kanion - 12000 - KWSM-12IR410ACF | Outdoor | Yes | Split | 12000 | 3.5172 | 1.2 | 2.931
6 | Kanion I 12 | Kanion | KWSM-12R410AHS16MV | Kanion - 12000 - KWSM-12R410AHS16MV |  | Yes | Split | 12000 | 3.5172 | 1.214 | 2.8972 | 3.8605 | 13.1712 | 4.9241 | 16.8
|  | Kanion | KWSM-18IR410ACF | Kanion - 18000 - KWSM-18IR410ACF | Outdoor |  | Split | 18000 | 5.2758 | 1.85 | 2.8518
7 | Kanion I 17 | Kanion | KWSM-18R410AHS16MV | Kanion - 17000 - KWSM-18R410AHS16MV |  | Yes | Split | 17000 | 4.9827 | 1.2907 | 3.8605 | 3.8605 | 13.1712 | 4.9241 | 16.8
|  | Kanion | KWSM-24IR410ACF | Kanion - 24000 - KWSM-24IR410ACF | Outdoor | Yes | Split | 24000 | 7.0344 | 2.25 | 3.1264
8 | Kanion I 24 | Kanion | KWSM-24R410AHS16MV | Kanion - 24000 - KWSM-24R410AHS16MV |  | Yes | Split | 24000 | 7.0344 | 1.8412 | 3.8206 | 3.8206 | 13.035 | 4.8361 | 16.5
|  | Lennox | 12ACXN036-230-22 | Lennox - 36000 - 12ACXN036-230-22 | Outdoor | Yes | Cassette | 36000 | 10.5516 |  | 3.3355 | 3.3355 | 11.38 | 3.8103 | 13
|  | Lennox | 13ACXN036-230-22 | Lennox - 36000 - 13ACXN036-230-22 | Outdoor | Yes | Cassette | 36000 | 10.5516 |  | 3.9744 | 3.9744 | 13.56 | 4.5431 | 15.5
|  | Lennox | LXG AHTC012100T4 | Lennox - 12000 - LXG AHTC012100T4 |  | Yes | Split | 12000 | 3.5172 | 1.1505 | 3.057 | 3.057 | 10.43 | 4.9241 | 16.8
|  | Lennox | LXG AHTC024100T4 | Lennox - 24000 - LXG AHTC024100T4 |  | Yes | Split | 24000 | 7.0344 | 2.43 | 2.8948 | 2.68 | 9.14
|  | Lennox | LXGAHT0018100T4 | Lennox - 18000 - LXGAHT0018100T4 |  |  |  | 18000 | 5.2758 | 1.75 | 3.0147 | 3.02 | 10.29
|  | Magic | M2GHP290-12 | Magic - 12000 - M2GHP290-12 | Indoor |  | Portable | 12000 | 3.5172 | 1.35 | 2.6053
|  | McQuay | MCS-104009-CCU215A | McQuay - 9000 - MCS-104009-CCU215A |  | No | Split | 9000 | 2.6379 | 0.97 | 2.7195
|  | McQuay | MCS-104012-CCU215A | McQuay - 12000 - MCS-104012-CCU215A |  |  | Split | 12000 | 3.5172 | 1.03 | 2.73
|  | McQuay | MCS-104024-CCU216A | McQuay - 24000 - MCS-104024-CCU216A |  |  | Split | 24000 | 7.0344 | 2.5213 | 2.79
|  | McQuay | MCS-104024-CWF215A | McQuay - 24000 - MCS-104024-CWF215A |  |  | Split | 24000 | 7.0344 | 1.83 | 3
|  | McQuay | MQIU-134024-HCU215A | McQuay - 23882.6339133402 - MQIU-134024-HCU215A |  |  | Split | 23882.6339 | 7 | 2.18 | 3
|  | McQuay | MQIU-164018-HCU215A | McQuay - 18000 - MQIU-164018-HCU215A |  |  | Split | 18000 | 5.2758 | 1.62 | 3.2567 |  |  |  |  | year 2020
|  | McQuay | MQIU-164024-HCU215A | McQuay - 24000 - MQIU-164024-HCU215A |  |  | Split | 24000 | 7.0344 | 2.8 | 2.5123 |  |  |  |  | year 2019
|  | McQuay | MQS-164024_CF215A | McQuay - 24000 - MQS-164024_CF215A |  |  | ceiling floor | 24000 | 7.1 | [6 empty] | year 2020
|  | MDV | MOCA30-21CDN1-QC2 | MDV - 21000 - MOCA30-21CDN1-QC2 | Outdoor | Yes | Split | 21000 | 6.1551 | 2.05 | 3.0025
|  | Midea | KFR-50GWS | Midea - 17059.0242238144 - KFR-50GWS |  |  | Split | 17059.0242 | 5 | 1.55 | 3.2258
|  | Midea | KFR-72GW | Midea - 24564.9948822927 - KFR-72GW |  |  | Split | 24564.9949 | 7.2 | 2.46 | 2.9268
|  | Midea | MOCA30-21CDN1-QC2 | Midea - 21000 - MOCA30-21CDN1-QC2 | Outdoor | yes | Split | 21000 | 6.1551 | 2.05 | 3.0025
|  | Midea | MSC-24CRN1 | Midea - 24000 - MSC-24CRN1 |  |  | Split | 24000 | 7.0344 | 2.4 | 2.931
|  | Miller | MDX5-036ECS3 | Miller - 36000 - MDX5-036ECS3 | Outdoor |  |  | 36000 | 10.5516
|  | MLB | MZW-24A4/EZ | MLB - 24000 - MZW-24A4/EZ |  |  | Split | 24000 | 7.0344 | 2.7 | 2.6053 |  |  |  |  | year 2014
|  | OTEC Omega | 80HW013J74-036DDV | OTEC Omega - 12300 - 80HW013J74-036DDV | indoor |  | VRF Split | 12300 | 3.6051 | [6 empty] | year 2014
|  | OTEC Omega | 81HM004J74-120MV7 | OTEC Omega - 48000 - 81HM004J74-120MV7 | Outdoor |  | Mini VRF | 48000 | 14.0688 | 4.36 | 3.2268 |  |  |  |  | year 2014
|  | OTEC Omega | 81HM004J94-120MV7 | OTEC Omega - 42000 - 81HM004J94-120MV7 | Outdoor |  | Mini VRF | 42000 | 12.3102 | 3.5 | 3.5172 |  |  |  |  | year 2014
|  | OTEC Omega | 82VC010J04-335DHV16 | OTEC Omega - 120000 - 82VC010J04-335DHV16 | Outdoor |  | combo VRF | 120000 | 35.172 | 9.23 | 3.8106 |  |  |  |  | year 2014
|  | OTEC Omega | IEFC026N3A-GWG100 | OTEC Omega - 36000 - IEFC026N3A-GWG100 | indoor |  | ceiling and floor | 36000 | 10.5516 | 4 | 2.6379
|  | OTEC Omega | TCHE024J0A | OTEC Omega - 24000 - TCHE024J0A | outdoor | Yes | Split | 24000 | 7.0344 | 2.1818 | 3.2241 | 3.2241 | 11
|  | Perfect Aire | PAC5000 | Perfect Aire - 5000 - PAC5000 |  |  | old model | 5000 | 1.4655 | 0.51546 | 2.8431 | 2.8431 | 9.7
|  | Pioneer |  | Pioneer - 24000 - |  |  | Cassette | 24000 | 7 | 2.1 | 3.3333
|  | Pioneer | AN013WLFARCAA3 | Pioneer - 12600 - AN013WLFARCAA3 |  |  | Split | 12600 | 3.6931 | 1.28 | 2.8852
|  | Pioneer | AN024WCFR10CA3 | Pioneer - 23882.6339133402 - AN024WCFR10CA3 | Outdoor |  | Split | 23882.6339 | 7 | 2.1 | 3.3333
|  | Polaris | TAC-12CSA/XA71 | Polaris - 12000 - TAC-12CSA/XA71 |  |  | Split | 12000 | 3.5172 | 1.21 | 2.9068 |  |  |  |  | R410
|  | Polaris | TAC-18CSA/XA71 | Polaris - 18000 - TAC-18CSA/XA71 |  |  | Split | 18000 | 5.2758 | 1.875 | 2.8138
|  | Polaris | TAC-24CSA/XA71 | Polaris - 24000 - TAC-24CSA/XA71 |  |  | Split | 24000 | 7.0344 | 2.3 | 3.0584
|  | Streamline | DC2404-EV | Streamline - 24000 - DC2404-EV |  | Yes | Split | 24000 | 6.45 | 2.08 | 3.101 |  |  |  |  | year 2022
|  | Streamline | FX1201-EV | Streamline - 12000 - FX1201-EV |  |  | Split | 12000 | 3.223 | 1.07 | 3.0121 |  |  |  |  | year 2019
|  | Streamline | FX2403-EV | Streamline - 20982.5997952917 - FX2403-EV |  |  | Split | 20982.5998 | 6.15 | [6 empty] | Year 2021
|  | Streamline | MCD-24HRFN8-Q | Streamline - 24000 - MCD-24HRFN8-Q | Indoor |  | Casette | 24000 | 7.0344
|  | Streamline | MCD-36HRFN8-Q | Streamline - 36000 - MCD-36HRFN8-Q | Indoor |  | Casette | 36000 | 10.5516
|  | Streamline | MOCA30U-24HFN1-Q | Streamline - 24000 - MOCA30U-24HFN1-Q | Outdoor |  | Casette | 24000 | 7.0344 | 2.085 | 3.3738
|  | Streamline | MOD30U-36HFN1-Q | Streamline - 36000 - MOD30U-36HFN1-Q | Outdoor |  | Casette | 36000 | 10.5516 | 2.715 | 3.8864
|  | Streamline | MOU-36HDN1 | Streamline - - MOU-36HDN1 |  |  | Split
|  | Streamline | TAC-12CHSA/BFI | Streamline - 12000 - TAC-12CHSA/BFI | outdoor | yes | Split | 12000 | 3.5172 | 1.07 | 3.2871 |  |  |  |  | R410A
|  | Streamline | TAC-12CSA - BH | Streamline - 12000 - TAC-12CSA - BH |  | No | Split | 12000 | 3.5172 | 1.28 | 2.7478
|  | Streamline | TAC-12CSA - KDI | Streamline - 12000 - TAC-12CSA - KDI | outdoor | No | Split | 12000 | 3.5172 | 1.095 | 3.2121
|  | Streamline | TAC-18CSA | Streamline - 18000 - TAC-18CSA |  |  | Split | 18000 | 5.2758 | 1.75 | 3.0147
|  | Streamline | TAC-24CHSA/BFI | Streamline - 24000 - TAC-24CHSA/BFI |  | yes | Split | 24000 | 7.0344 | 2.19 | 3.2121 |  |  |  |  | R410A
|  | Streamline | TAC-24CSA | Streamline - 24000 - TAC-24CSA |  |  | Split | 24000 | 7.0344 | 2.9 | 2.4257
|  | TCL | TAC-12CSA/KCI | TCL - 12000 - TAC-12CSA/KCI |  | Yes | Split | 12000 | 3.5172 | 1.095 | 3.2121
|  | TCL | TAC-12CSAI | TCL - 12000 - TAC-12CSAI |  |  | Split | 12000 | 3.5172 | 1.28 | 2.7478 | 3.24
|  | TCL | TAC-18CHSA/KCI | TCL - 18000 - TAC-18CHSA/KCI |  | Yes | Split | 18000 | 5.2758 | 1.63 | 3.2367
|  | TCL | TAC-18CHSA/XA51 | TCL - 18000 - TAC-18CHSA/XA51 |  | No | Split | 18000 | 5.2758 | 1.665 | 3.1686
|  | TCL | TAC-24CHSA/XA51 | TCL - 24000 - TAC-24CHSA/XA51 |  | Yes | Split | 24000 | 7.0344 | 2.51 | 2.8025
|  | TCL | TAC-24CHSA/XKCI | TCL - 24000 - TAC-24CHSA/XKCI |  | Yes | Split | 24000 | 7.0344 | 2.19 | 3.2121
|  | TCL | TAC-24CSA/HD | TCL - 24000 - TAC-24CSA/HD | outdoor |  | Split | 24000 | 7.0344 | 2.9 | 2.4257
|  | TCL | TAC-24CSAI | TCL - 24000 - TAC-24CSAI |  | Yes | Split | 24000 | 7.0344 | 2.175 | 3.2342
|  | Temp Blue | TBF41B-036-HYH1C | Temp Blue - 36000 - TBF41B-036-HYH1C |  |  | Ceiling and floor | 36000 | 10.5516 | [6 empty] | year 2023
|  | Temp Blue | TBG41G-018PH3U2C | Temp Blue - 18000 - TBG41G-018PH3U2C |  |  | Split | 18000 | 5.2758 | 1.865 | 2.8288 | 2.8313 | 9.66
|  | Temp Blue | TBH43FX012-H7N1C | Temp Blue - 12000 - TBH43FX012-H7N1C |  |  | Split | 12000 | 3.5172 | [6 empty] | year 2023
|  | TRANE | 4TVH0055BD000AA | TRANE - - 4TVH0055BD000AA |  |  | Heat Pump |  | 15.5
|  | TRANE | 4TVH0086BD000AA | TRANE - - 4TVH0086BD000AA |  |  | Heat Pump |  | 25.2
|  | TRANE | 4TVH0140BD000AA | TRANE - - 4TVH0140BD000AA |  |  | Heat Pump |  | 40
|  | Universal | MRSVX36AS | Universal - 36000 - MRSVX36AS | Outdoor | Yes | Split | 36000 | 10.5516 | 4.5 | 2.3448 |  |  |  |  | Year 2017
|  | VTCool | VTCool | VTCool - 24000 - VTCool |  |  | Split | 24000 | 7.0344 | 2.66 | 2.6445
|  | Westinghouse | WIWXL-18ENW1 | Westinghouse - 18000 - WIWXL-18ENW1 |  |  | Split | 18000 | 5.2758 | 1.89 | 2.7914
|  | Westpoint | WiM-1821.L | Westpoint - 18000 - WiM-1821.L |  | Yes | Split | 18000 | 5.2758 | 1.643 | 3.2111
|  | Westpoint | WIM-2418L | Westpoint - 22000 - WIM-2418L |  | Yes | Split | 22000 | 6.4482 | 2.009 | 3.2097
|  | Westpoint | WIM-2421L | Westpoint - 24000 - WIM-2421L |  | Yes | Split | 24000 | 7.0344 | 2.269 | 3.1002
|  | Westpoint | WIZ-1212-LE | Westpoint - 12000 - WIZ-1212-LE |  | yes | Split | 12000 | 3.5172 |  | 3.06
|  | Westpoint | WIZ-12217-LHE | Westpoint - 12071 - WIZ-12217-LHE |  | yes | Split | 12071 | 3.538 | 0.995 | 3.057 | 3.057 | 10.43 | 1.7879 | 6.1
|  | Westpoint | WIZ-2412-LE | Westpoint - 24000 - WIZ-2412-LE |  |  | Split | 24000 | 7.0344 |  | 3.1
|  | Westpoint Eolia | WSG-129E | Westpoint Eolia - 10917.7755032412 - WSG-129E |  |  | Split | 10917.7755 | 3.2 | 1.2 | 2.6667
|  | Westpoint Eolia | WSM.18.LE | Westpoint Eolia - 18000 - WSM.18.LE |  |  | Split | 18000 | 5.2758 | 1.64 | 3.217
|  | Westpoint Eolia | WSM.247 | Westpoint Eolia - 24000 - WSM.247 |  |  | Split | 24000 | 7.0344 | 2.4 | 2.931
|  | York | YHKE12ZEEAXO-RX | York - 11430 - YHKE12ZEEAXO-RX |  | Yes | Split | 11430 | 3.3501 | 1.162 | 2.8831
|  | York | YHKE24XEEAXA-RX | York - 23035 - YHKE24XEEAXA-RX |  | Yes | Split | 23035 | 6.7516 | 2.633 | 2.5642
|  | York | YUJN24BYNNETH1 | York - 24000 - YUJN24BYNNETH1 |  |  | Casette | 24000 | 7.0344 | 2.23 | 3.1544
|  |  | Other specify | Other specify | [11 empty] | 3.05 a 3.2 el COP

## PV assessment
PV ASSESSMENT
| Assessment of the PV installation potential | [6 empty] | Yes
No
| Physical space N°1 | [5 empty] | Area description
GPS coordinates
|  | Type of area for PV panels |  |  |  | (roof, carpark, open ground)
|  | Available space (m2) |  | Azimuth angle
In case of roofop, describe material:
|  | Current tilt of space (°) |  |  | Required tilt for panels (°)
Current use of space
Access and security
| Physical space N°2 | [5 empty] | Area description
GPS coordinates
|  | Type of area for PV panels |  |  |  | (roof, carpark, open ground)
|  | Available space (m2) |  | Azimuth angle
In case of roofop, describe material:
|  | Current tilt of space (°) |  |  | Required tilt for panels (°)
Current use of space
Access and security
| Physical space N°3 | [5 empty] | Area description
GPS coordinates
|  | Type of area for PV panels |  |  |  | (roof, carpark, open ground)
|  | Available space (m2) |  | Azimuth angle
In case of roofop, describe material:
|  | Current tilt of space (°) |  |  | Required tilt for panels (°)
Current use of space
Access and security
Electrical Installation
Type of electrical connection (three-phase or single-phase, status and photos)
Describe distance from panel to the panels's location. Electrical panel location in Google earth
Contracted power of the building (kW)
Cable sections size (mm)
Capacity of the main switch (Amps)
Measure current demand (Amps)
Measure current demand (kW)
Comments:
Areas need to be marked on a google earth image or map, described in terms of characteristics, challenges, requirements, roof conditions, etc. Photos are required.Shades and obstacles. Distance to keep from any structure or space. Describe, meaure heights, take pictures.

## 21Photos checklist (hidden)
19. PHOTOS & THERMOGRAPHIES
| 38 | Picture's Checklist
|  |  | Place or equipment | Description
|  | 1 | Front
|  | 2 | Plant
|  | 3 | Product
|  | 4 | Windows detail
|  | 5 | Roof detail
|  | 6 | Roof space
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## 22.Parameter's calculation-EEMM (hidden)
*variables identificación
20.Parameter's calculation-EEMM
| EEM 1. Efficient lighting | EEM 2. Automatic lighting control |  | EEM 3. Pipe insulation |  | EEM 4. Tank isolation | EEM 5. Furnace insulation | EEM 6. Cold chamber isolation
|  | % reduction in hours |  | Section |  | Tank | Surface to isolate | Surface to isolate
|  | Control system type |  | Associated equipment |  | Associated equipment | Associated furnace | Associated chamber
|  |  |  | Energy source |  | Energy source | Fuel | Area
|  |  |  | Length |  | Height | Area | Yield / COP
|  |  |  | Diameter |  | Diameter | Yield / COP | Surface temperature
|  |  |  | Yield / COP |  | Yield / COP | Surface temperature | Ambient temperature
|  |  |  | Pipe temperature |  | Pipe temperature | Ambient temperature
|  |  |  | Ambient temperature |  | Ambient temperature
| EEM 7. Efficient drives | EEM 8. Combustion adjustment |  | EEM 9. VSD in pumps and fans |  | EEM 10. Pressure reduction in compressed air | EEM 11. Leak reduction campaign | EEM 12. VSD in compressed air compressors
| Equipment and quantity | Equipment, brand, model |  | Equipment, brand, model |  | Current working pressures (pressure gauge readings) | Current leak's energy consumption | Relieve variation in demand
|  | Fuel |  | Type (pump/fan)
| % of time in every load range (25%, 50%, 75%, over 90%) | Thermal power |  | % of time in every load range (25%, 50%, 75%, over 90%) |  | Required working pressures
|  | Current efficiency |  |  |  | Reduction Recommendation
Combustion previous measures
| EEM 13. Reduction of evaporation temperature in refrigeration systems |  | EEM 14. Split's control |  | RE1. Thermal solar panels |  | RE2. Fotovoltaic panels
| Equipment/Chamber Type |  | Equipment |  | Current team that would replace |  | Maximum area to install
| Zone/Position in cooling system |  | Zone/Use |  | Temperature set point |  | Surface orientation and inclination
| Associated equipment |  | % time loaded |  | Maximum area for installation |  | Distance from surface to supply
| Evaporator temperature |  | Number of splits involved
Refrigerant
Temperature of use
Thermal power
| ACE 1 |  | ACE 2 |  | ACE 3
Note on Z16: fghiardo/asarachik if they have any study done of losses or perform at the moment

## 21.EEM1 (hidden)
21. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 22.EEM2 (hidden)
22. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 23.EEM3 (hidden)
23. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 24.EEM4 (hidden)
24. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 25.EEM5 (hidden)
25. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 24.EEM6 (hidden)
26. EEM
1 | EEM Identification
Name of EEM
2 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## 27.Other EEM (hidden)
27. EEM
1 | EEM Identification
Name of EEM
2 | Description
3 | Survey of parameters
|  |  | Name | Value | Unit | Value's source (data, measurement, survey) | Comments (assumptions, difficulties, etc.)
1
2
3
4
5
6
7
8
3 | Measurement description:
Technical description of the measure with justification for its recommendation, the equipment involved and/or technical parameters involved
4 | Technical recommendations:
Describe technical requirements to implement the measure, such as: detailed list of equipment and materials, necessary human resources, aspects to be taken into account (eg, the need to stop the production line, do it during working hours, etc.)

## Consumption
Consumption
|  | Electric energy | Diesel | LPG | Total
| Annual Consumption (kWh) | 244638 | 0 | 0 | 244638
| Consumption (%) | 100% | 0% | 0% | 100%
| Annual Cost (XCD) | 252591.0723 | 0 | 0 | 252591.0723
| Cost (%) | 100% | 0% | 0% | 100%
| Cost (USD) | 126295.5361 | 0 | 0 | 126295.5361
| Cost (USD/kWh) | 0.51625 | #DIV/0! | #DIV/0! | 0.51625
| Indicator (kWh/m2) | 244.638 | 0 | 0 | 244.638
| Mean (kW) | 356532
| Electricity consumption |  |  |  |  | Diesel | [6 empty] | LPG
|  |  | Equivalence | 8.6e-05 | toe/kWh
| Electricity | month | Year | Total monthly Energy (kWh) | Total Cost (BBD) - VAT included | Diesel | month | Year | Gallons | Total monthly Energy (kWh) | Total Cost (XCD) - VAT included |  | LPG | month | Year | kg | Total monthly Energy (kWh) | Total Cost (XCD) - VAT included
|  | 2020-09-01 |  | 25255 | 26076.0288
|  | 2020-10-01 |  | 30213 | 31195.2112
|  | 2020-11-01 |  | 20753 | 21427.6708
|  | 2020-12-01 |  | 21506 | 22205.1505
|  | 2021-01-01 |  | 18448 | 19047.7363
|  | 2021-02-01 |  | 22993 | 23740.4922
|  | 2021-03-01 |  | 21730 | 22436.4326
|  | 2021-04-01 |  | 22283 | 23007.4104
|  | 2021-05-01 |  | 20032 | 20683.2314
|  | 2021-06-01 |  | 21560 | 22260.906
|  | 2021-07-01 |  | 17465 | 18032.7794
|  | 2021-08-01 |  | 17920 | 18502.5712
|  | 2021-09-01 |  | 20398 | 21061.1299 |  | January
|  | 2021-10-01 |  | 19580 | 20216.5371 |  | February
|  | 2021-11-01 |  | 21758 | 22465.3429 |  | March
|  | 2021-12-01 |  | 21632 | 22335.2467 |  | April
|  | 2022-01-01 |  | 15701 | 16211.4325 |  | May
|  | 2022-02-01 |  | 19003 | 19620.7791 |  | June
|  | 2022-03-01 |  | 17735 | 18311.5569 |  | July
|  | 2022-04-01 |  | 21131 | 21817.9594 |  | August
|  | 2022-05-01 |  | 20998 | 21680.6356 |  | September
|  | 2022-06-01 |  | 20519 | 21186.0635 |  | October
|  | 2022-07-01 |  | 24229 | 25016.674 |  | November
|  | 2022-08-01 |  | 21954 | 22667.7147 |  | December | [12 empty] | XCDkg 2022
|  | mean |  | 20849.6087 | 21527.4202 |  | mean |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | mean |  | 0 | 0 | 0 |  | 5.36
|  | Annual |  | 244638 | 252591.0723 |  | Annual |  | 0 | 0 | 0 | 0 |  | Annual |  | 0 | 0 | 0 | 0
|  | unit cost (EC/kWh) |  | 1.0325 |  |  | unit cost |  | (XCD/lt) | #DIV/0! |  |  |  | unit cost |  | (XCD/kg) | #DIV/0!
Diesel oil consumption

## Lighting
Lighintg inventory
| Total | [13 empty] | 23679.8 | 38454.1776
| Percentage | [14 empty] | 15.72%
#REF!
[15 empty] | Cálculos |  | #REF!
| Zone | Foto | Type | Altura | Nro_fixtures | Lamp_x_fix | Quantity | Power lamp (W) | % con impedancia magnética | Control | Daily use (h/day) | Annual use (day/year) | Total (h/year) | Observaciones | Pot_sist (W) | Consumption (kWh/año) | #REF!
1 | Lobby |  | Fluorescent lamp |  | 6 | 1 | 6 | 15 | 0% | 0 | 6 | 276 | 1656 |  | 90 | 149.04 | #REF!
2 | Seminar roomx3 |  | Fluorescente tube |  | 36 | 2 | 72 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 2721.6 | 4506.9696 | Incandescent
3 | Bathroom x 4 |  | Fluorescente tube |  | 20 | 1 | 20 | 36 | 0% | 0 | 6 | 276 | 1656 | La mitad están fundidas | 756 | 1251.936 | Fluorescent lamp
4 | Computer Lab |  | Fluorescente tube |  | 32 | 2 | 64 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 2419.2 | 4006.1952 | Fluorescente tube
5 | Storage x 2 |  | Fluorescente tube |  | 4 | 2 | 8 | 36 | 0% | 0 | 2 | 276 | 552 | Trabajador Social. 175 Lux | 302.4 | 166.9248 | Fluorescente tube short
6 | Hallway |  | LED lamp |  | 2 | 1 | 2 | 10 | 0% | 0 | 6 | 276 | 1656 | Oficina Psicología | 20 | 33.12 | PLL
7 | Hallway |  | Fluorescent lamp |  | 3 | 1 | 3 | 15 | 0% | 0 | 6 | 276 | 1656 |  | 45 | 74.52 | T12 fluorscent tube
8 | Staff room |  | Fluorescente tube |  | 4 | 2 | 8 | 36 | 0% | 0 | 6 | 276 | 1656 | Oficina Psicología | 302.4 | 500.7744 | Halogen
9 | Lecture Room |  | Fluorescente tube |  | 12 | 2 | 24 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 907.2 | 1502.3232 | halogen projector lamp
10 | Lecture Room |  | Fluorescente tube |  | 2 | 1 | 2 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 75.6 | 125.1936 | Sodum (HPS)
11 | Lecture room Nr2 |  | Fluorescente tube |  | 24 | 2 | 48 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 1814.4 | 3004.6464 | AR111
12 | Lecture room Nr2 |  | Fluorescente tube |  | 2 | 1 | 2 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 75.6 | 125.1936 | LED (projector, otros)
13 | Cafeteria |  | Fluorescente tube |  | 6 | 2 | 12 | 36 | 0% | 0 | 0 | 0 | 0 |  | 453.6 | 0
14 | Lecture room nNr3 |  | Fluorescente tube |  | 20 | 2 | 40 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 1512 | 2503.872
15 | Lecture room nNr3 |  | Fluorescente tube |  | 2 | 1 | 2 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 75.6 | 125.1936
16 | Lecture Room Nr4 |  | Fluorescente tube |  | 20 | 2 | 40 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 1512 | 2503.872
17 | Lecture Room Nr4 |  | Fluorescente tube |  | 2 | 1 | 2 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 75.6 | 125.1936
18 | Theatre Nr2 |  | Fluorescente tube |  | 36 | 2 | 72 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 2721.6 | 4506.9696
19 | Theatre Nr1 |  | Fluorescente tube |  | 64 | 2 | 128 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 4838.4 | 8012.3904
20 | Theatre Nr1 |  | Fluorescent lamp |  | 8 | 1 | 8 | 15 | 0% | 0 | 6 | 276 | 1656 |  | 120 | 198.72
21 | Theatre Nr3 |  | Fluorescente tube |  | 36 | 2 | 72 | 36 | 0% | 0 | 6 | 276 | 1656 |  | 2721.6 | 4506.9696
22 | Exterior |  | Fluorescent lamp |  | 8 | 1 | 8 | 15 | 0% | 0 | 12 | 364 | 4368 |  | 120 | 524.16
23 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
24 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
25 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
26 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
27 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
28 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
29 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
30 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
31 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
32 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
33 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
34 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
35 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0

## Refrigeration
Refrigeration systems and equipment
[16 empty] | TOTAL |  | 0 | 0.3 | 6600
[16 empty] | SUB TOTAL | Fridges | 0 | 0.3 | 6600
[16 empty] | SUB TOTAL | Cold Chamber | 0 | 0 | 0
[16 empty] | SUB TOTAL | Ice Machines | 0 | 0 | 0
[16 empty] | PORCENTAJE |  | - | - | 2.698%
| System | Brand/model | Type | Quantity | Thermal power (kW) | Power (kW) | COP | Temperature (ºC) | Temp Set point (ºC) | VSD | Freq VSD | % time in load | Hours/day | Days/week | Weeks/year | Comments |  | Thermal_P (kW) | Electric_P (kW) | Consumption (kWh/year)
LISTAS
| Fridges | 0 | Small | 1 |  | 0.3 |  | 5 | 7 |  |  | 30% | 24 | 7 | 52 | 0 |  | 0 | 0.3 | 1200 | Interior
| Freezer | 0 | Horizontal 2 door freezer | 3 |  | 0.5 |  | 0 | 0 |  |  | 30% | 24 | 7 | 52 | 0 |  | 0 | 1.5 | 5400 | Exterior
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  | 30% | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | Freezer
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Fridges
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Cold Chamber
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Ice Machines
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Other
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Yes
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | No
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[18 empty] | 0 | 0 | 0

## Transporte (hidden)
Transporte | [12 empty] | LISTAS
Eléctrico
[9 empty] | 0 | 0 | 0 | 0 | Gasoil
[9 empty] | - | #DIV/0! | #DIV/0! | #DIV/0! | GLP
Consumos anuales
| Tipo | Cantidad | Combustible | Potencia motor (HP) | Uso (h/día) | Días/semana | Semanas/año | Consumo mensual (kWh/lt/kg) | Pot (kW) | Electricidad (kWh/año) | Gas oil (lt/año) | GLP (kg/año)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
[10 empty] | 0 | 0 | 0
Note on J7: Federico González Madina: En caso de conocerlo, ingresar el consumo mensual para el energético correspondiente: -lt para gas oil -kg GLP -kWh para electricidad En otro caso, ingresar rendimiento y km de uso para determinar el consumo.

## Datos generales (hidden)
Datos Generales
Descripción del proceso productivo
Nombre de la empresa
| Responsable | Nombre
Teléfono móvil
| Emplazamiento | Dirección
Provincia
Municipio
| Datos a completar |  |  |  |  | Sistemas que asisten al sistema productivo
Número de trabajadores
Rubro
| Producción / Venta |  | Producto | Cantidad
| Horario Funcionamiento | Lunes - Viernes |  |  | h
|  | Fin de semana |  |  | h
|  | Otros |  |  | h
| Antigüedad |  |  |  | año
Nº plantas
| Superfície útil | Total
¿Instalación Solar?
| Datos | Tipología
Nº paneles
Orientación
Inclinación
¿Instalación Fotovoltaica?
| Datos | Tipología
Nº paneles
Orientación
Inclinación
Note on M3: Federico González Madina: Descripción del proceso desde que entra la materia prima hasta que se tiene el producto terminado o para la venta
Note on M15: Federico González Madina: Sistemas que acompañan al sistema productivo como cámaras de frío, sistemas de aire comprimido, etc.

## Equipment
Equipment
| TOTALES | [13 empty] | 4758.24 | 0 | 4758.24
| PORCENTAJE | [13 empty] | #DIV/0! | #DIV/0! | 1.945%
| Zone | Device | Model | Quantity | Power (kW) | Potencia SB (W) | On/Off | hours/day | days/ week | weeks/ year | % time ON | Observaciones | Pot_inst (kW) ON | Pot_inst (kW) SB | Consumo (kWh/año) ON | Consumo (kWh/año) SB | Consumo total (kWh/año)
| Lobby | TV | 32" | 1 | 0.1 |  |  | 12 | 6 | 46 | 100% |  | 0.1 | 0 | 331.2 | 0 | 331.2
| Lobby | Fan |  | 1 | 0.1 |  |  | 6 | 6 | 46 | 100% |  | 0.1 | 0 | 165.6 | 0 | 165.6
| Seminar rooms | Projector |  | 3 | 0.3 |  |  | 6 | 6 | 46 | 20% |  | 0.9 | 0 | 298.08 | 0 | 298.08
| Computer LAB | PC |  | 40 | 0.05 |  |  | 4 | 6 | 46 | 100% |  | 2 | 0 | 2208 | 0 | 2208
| Computer LAB | Printer |  | 3 | 0.1 |  |  | 1 | 6 | 46 | 20% |  | 0.3 | 0 | 16.56 | 0 | 16.56
| Lecture rooms | Projector |  | 4 | 0.3 |  |  | 6 | 6 | 46 | 50% |  | 1.2 | 0 | 993.6 | 0 | 993.6
| Theatres | Projector |  | 3 | 0.3 |  |  | 6 | 6 | 46 | 50% |  | 0.9 | 0 | 745.2 | 0 | 745.2
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | 0

## Pumps
Inventory
LISTA
[18 empty] | 1.5 |  | 3276 | 0 | Electricity
[18 empty] | - |  | 1.339% | #DIV/0! | Gas oil
kW
| Identification | Model/branch | Use | Type | Quantity | Energetic | Power (kW) | Power meassured (kW) | VSD (Yes/No) | Frequency VSD (Hz) | Use (h/day) | % time load | Days/week | Monthly (kWh) | Weeks/year | Total (h/year) | Notes | Power_inst (kW) | Power meassured (kW) | Consumption (kWh/year) | Consumption Gas oil (lt/year)
| Pump | Lowara | potable water | pump | 2 | Electricity | 1.5 | 0 | 0 |  | 24 | 25% | 7 |  | 52 | 8736 | One for back up | 1.5 | 0 | 3276 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | Electricity | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0
Note on P7: Federico González Madina: Solo gas oil

## Hot water (hidden)
Agua caliente sanitaria, de proceso y calefacción
[22 empty] | Pot_inst térmica(kW) | Pot_inst consumida (kW) | Electricidad (kWh/año) | Gas nat. (m3/año) | Gas oil (lt/año) | GLP (kg/año) | Biomasa (kg/año)
[20 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | SUB TOTAL | ACS | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | SUB TOTAL | AC Proceso | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | SUB TOTAL | AC calefacción | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | PORCENTAJE |  | - | - | 0% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Consumos anuales
| Zona | Equipo | Foto | Tipo de uso | Uso final | Energético | Unidades | Potencia térmica (kW) | Rendimiento / COP | Potencia consumida (kW) | Acumulador (lt) | Temp AC (ºC) | Uso diario (m3/dia) | Uso diario (horas/dia) | Uso mensual (dias/mes) | Uso anual (meses/año) | Uso (m3/mes) | Consumo mensual (kWh/lt/m3/kg) | Consumo mensual calculado (kWh) | Observaciones |  | Pot_inst térmica(kW) | Pot_inst consumida (kW) | Electricidad (kWh/año) | Gas nat. (m3/año) | Gas oil (lt/año) | GLP (kg/año) | Biomasa (kg/año) | listas
| CALDERA AC, TERMOS, ACUMULADORES, BOMBA CALOR ACS | [27 empty] | Electricidad | ACS
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas Natural | AC proceso
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas oil | AC calefacción
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GLP
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Biomasa
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | [6 empty] | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Consumos de referencia
[5 empty] | Tipo de edificación |  | Consumo AC 45ºC (lt/persona.dia)
[5 empty] | Viviendas |  | 40
[5 empty] | Hotel **** |  | 80
[5 empty] | Residencia |  | 60
[5 empty] | Vestuarios/duchas colectivas |  | 30
[5 empty] | Fábricas y talleres |  | 30
[5 empty] | Oficinas |  | 3
[5 empty] | Gimnasios |  | 30
[5 empty] | Restaurantes |  | 12
Note on T10: Federico González Madina: En caso de conocerlo, ingresar el consumo mensual para el energético correspondiente: -lt para gas oil -kg para biomasa y GLP -m3 para Gas natural -kWh para electricidad De no conocerlo se calcula en la celda de la derecha, a partir del consumo de agua caliente y el rendimiento del equipo
Note on U10: Federico González Madina: Consumo calculado a partir del uso de agua caliente. Se debe conocer el consumo de agua caliente mensual y el rendimiento del equipo

## Compr. Air
Compressed air equipment and systems
[15 empty] | TOTAL | 0 | 0
[15 empty] | PORCENTAGE | - | 0%
| Device | Usage | Foto | Nominal Power (kW) | Set pressure (bar) | VSD | Hours/day | Days/week | Week/year | % on load | % on discharge | Power on load (kW) | Power on discharge (kW) | Consumption (kWh/year) | Observation | Pot_inst (kW) | Consumption (kWh/year)
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0

## Ventilation
Ventilation
[17 empty] | 0 | 0 | Si
[18 empty] | 0% | No
| Identification | Model/branch | Use | Type | Quantity | Power (kW) | Power meassured (W) | VSD (Yes/No) | Frequency VSD (Hz) | Use (h/day) | % time load | Days/week | Weeks/year | Total (h/year) | Notes | Pow_inst (kW) | Pow_meassured (kW) | Consumption (kWh/año)
| Pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100% | 0 | 0 | 0 |  | 0 | 0 | 0
Note on O22: Federico González Madina: Solo gas oil
Note on Q34: Federico González Madina: Solo gas oil

## AC
Air conditioners
TOTALES | [14 empty] | TOTAL |  |  | 127.0534 | 173255.1781
[15 empty] | SUB TOTAL |  | AC | 40.395 | 53515.296
[15 empty] | SUB TOTAL |  | Central AC | 86.6584 | 119739.8821
PORCENTAJE | [18 empty] | 70.82%
| # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations |  | Pot_inst (kW) | Consumption (kWh/year)
| 1 | Seminar room | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 60% | 0 |  | 2.31 | 3060.288
| 2 | Seminar room 2 | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 60% | 0 |  | 2.31 | 3060.288
| 3 | Seminar room 3 | AC | Split | Daikin | 1 | 2.01 | 3.21 | 2.01 | 0 | 21 | 8 | 6 | 46 | 60% | 0 |  | 2.01 | 2662.848
| 4 | Computer Lab | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 2.05 | 2715.84
| 5 | Computer Lab | AC | Split | Delta | 1 | 2.18 | 3.23 | 2.18 | 0 | 25 | 8 | 6 | 46 | 60% | 0 |  | 2.18 | 2888.064
| 6 | Computer Lab | AC | Split | Westinghouse | 1 | 1.89 | 2.79 | 1.89 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 1.89 | 2503.872
| 7 | Lecture Room | AC | Split | Lennox | 1 | 2.43 | 2.89 | 2.43 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 2.43 | 3219.264
| 8 | Lecture Room | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 60% | 0 |  | 2.43 | 3219.264
| 9 | Lecture room Nr2 | AC | Split | Midea | 2 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 60% | 0 |  | 4.86 | 6438.528
| 10 | Lecture room nNr3 | AC | Split | Daikin | 2 | 2.01 | 3.21 | 2.01 | 0 | 25 | 8 | 6 | 46 | 60% | 0 |  | 4.02 | 5325.696
| 11 | Lecture room nNr3 | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 2.05 | 2715.84
| 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 2.9 | 2.43 | 2.9 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 2.9 | 3841.92
| 13 | Lecture Room Nr4 | AC | Split | TCL | 3 | 2.175 | 3.23 | 2.175 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 6.525 | 8644.32
| 14 | Lecture Room Nr4 | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 24 | 8 | 6 | 46 | 60% | 0 |  | 2.43 | 3219.264
| 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 14.5664 | 19297.5753
| 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 23.1753 | 3 | 23.1753 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 46.3506 | 61405.2116
| 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 14.5664 | 19297.5753
| 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 7.45 | 9869.76
| 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 3.725 | 4934.88
| 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 60% | 0 |  | 3.725 | 4934.88
| 21 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 22 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 23 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 24 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 25 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 26 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 27 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 28 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 29 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 30 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 31 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 32 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 33 | 0 | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
[10 empty] | 0 | 0

## Fuerza Motriz (hidden)
INVENTARIO DE MOTORES ELÉCTRICOS INSTALADOS
| SUBTOTALES | [11 empty] | 0 | 0 | 0
| PORCENTAJE | [13 empty] | #DIV/0!
| Nombre del equipo | Cantidad (n°) | Clase de motor | Potencia nominal (kW) | Potencia medida (kW) | Factor de pot. Medido | Factor de carga promedio (%) | Uso diario (h/dia) | Días/semana | Semanas/año | Uso total (h/año) | Observaciones | Pot_inst (kW) | Pot_medida (kW) | Consumo total (kWh/año)
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 |  | 0 | 0 | 0

## Hornos (hidden)
Hornos
[12 empty] | Electricidad (kWh/año) | Gas nat. (m3/año) | Gas oil (lt/año) | GLP (kg/año) | Biomasa (kg/año)
[10 empty] | TOTAL | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | PORCENTAJE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Consumos anuales
| Equipo | Foto | Uso | Energético | Unidades | Uso diario (horas/dia) | Días por semana | Semanas al año | Consumo mensual (kWh/lt/m3/kg) | Observaciones |  | Electricidad (kWh/año) | Gas nat. (m3/año) | Gas oil (lt/año) | GLP (kg/año) | Biomasa (kg/año)
| Horno 1 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
| Horno 2 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | listas
| Horno 3 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | Electricidad
| Horno 4 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | Gas Natural
| Horno 5 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | Gas oil
GLP
Biomasa

## Balance
Total uses |  |  | Electricity uses |  |  | Diesel uses |  |  | LPG uses
Energy Use | Annual consumption (kWh) | % | Energy Use | Annual consumption (kWh) | % | Energy Use | Annual consumption (kWh) | % | Energy Use | Annual consumption (kWh) | %
Lighting | 38454.1776 | 15.72% | Lighting | 38454.1776 | 15.72% | Lighting |  | #DIV/0! | Lighting |  | #DIV/0!
Equipment | 4758.24 | 1.945% | Equipment | 4758.24 | 1.945% | Equipment |  | #DIV/0! | Equipment |  | #DIV/0!
Compressed air | 0 | 0% | Compressed air | 0 | 0% | Compressed air |  | #DIV/0! | Compressed air |  | #DIV/0!
Electrical motors | 0 | 0% | Electrical motors | 0 | 0% | Electrical motors |  | #DIV/0! | Electrical motors |  | #DIV/0!
Vent | 0 | 0% | Vent | 0 | 0% | Vent |  | #DIV/0! | Vent |  | #DIV/0!
Pump | 3276 | 1.339% | Pump | 3276 | 1.339% | Pump | 0 | #DIV/0! | Pump |  | #DIV/0!
Hot water | 0 | 0% | Hot water | 0 | 0% | Hot water | 0 | #DIV/0! | Hot water | 0 | #DIV/0!
Ovens | 0 | 0% | Ovens | 0 | 0% | Ovens | 0 | #DIV/0! | Ovens |  | #DIV/0!
Heat | 0 | 0% | Heat | 0 | 0% | Heat | 0 | #DIV/0! | Heat | 0 | #DIV/0!
Freezers/Fridges | 6600 | 2.698% | Freezers/Fridges | 6600 | 2.698% | Freezers/Fridges |  | #DIV/0! | Freezers/Fridges |  | #DIV/0!
Ice machines | 0 | 0% | Ice machines | 0 | 0% | Ice machines |  | #DIV/0! | Ice machines |  | #DIV/0!
AC units | 53515.296 | 21.88% | AC units | 53515.296 | 21.88% | AC units | 0 | #DIV/0! | AC units |  | #DIV/0!
Central AC | 119739.8821 | 48.95% | Central AC | 119739.8821 | 48.95% | Central AC |  | #DIV/0! | Central AC |  | #DIV/0!
Transport | 0 | 0% | Transport | 0 | 0% | Transport | 0 | #DIV/0! | Transport |  | #DIV/0!
Others | 18294.4043 | 7.478% | Others | 18294.4043 | 7.478% | Others | 0 | #DIV/0! | Others |  | #DIV/0!
TOTAL | 244638 | 100% | TOTAL | 244638 | 100% | TOTAL | 0 | #DIV/0! | TOTAL | 0 | #DIV/0!

## Conversions
Conversión energéticos |  |  |  |  | Factor de emisión (kgCO2/kg)
Electricidad | 8.6e-05 | tep/kWh | 1 | kWh/kWh
Gas Natural | 0.00083 | tep/m3 | 9.6512 | kWh/m3 | 3.76 | kgCO2/m3
Gas oil | 0.000868 | tep/lt | 10.093 | kWh/lt | 3.73 | kgCO2/lt
GLP | 0.00109 | tep/kg | 12.6744 | kWh/kg | 2.88 | kgCO2/kg
Biomasa | 0.000201 | tep/kg | 2.3372 | kWh/kg | 3.14 | kgCO2/kg
|  |  | $2.60/lb | 0.96296 | 2.1257 | 0.16772
|  |  | GLP | USD/lb | USD/kg | USD/kWh
0

## EEM1
Efficient lighting
Unitary energy cost (USD/kWh) | lifespan (years) | Tasa de descuento | Exchange rate | Tec | Savings | Unitary cost (USD/unid)
0.51625 | 10 | 6% | 2 | #REF! | 90% | 5.7 | Babardos | Lights for replacement | [11 empty] | Savings
|  |  |  | #REF! | 63% | 5.7 |  | Zone | Type | height | Nro_fixtures | Lamp_x_fix | Power lamp (W) | Impedance | Control | Daily (h/day) | Annual use (day/year) | Total (h/year) | Conumpion (kWh/year) | New consumption (kWh/año) | Savings (kWh) | Ahorro (USD/año) | Unitary cost (USD/unid) | Inversion (USD) | Lugar | Tipo_Lamp | Nro Lum | Lamp_x_Lum | Pot_Lamp (W) | Uso total (h/año) | Pot_sist (W) | Consumo (kWh/año)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (tonCO2/year) | #REF! | 50% | 17.7 |  | Lobby | Fluorescent lamp |  | 6 | 0 | 0 | 6 | 15 | 6 |  | 1656 | 149.04 | 74.52 | 74.52 | 38.4713 | 403 | 2418 | Lobby | Fluorescent lamp | 0 | 0 | 6 | 6 | 0 | 1656
#N/A | #N/A | #N/A | #N/A | #REF! | 0% | 0 |  | Seminar roomx3 | Fluorescente tube |  | 72 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 4506.9696 | 2253.4848 | 2253.4848 | 1163.3723 | 0 | 0 | Seminar roomx3 | Fluorescente tube | 0 | 0 | 72 | 6 | 0 | 1656
|  |  |  | Incandescent | 0% | 0 |  | Bathroom x 4 | Fluorescente tube |  | 20 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 1251.936 | 625.968 | 625.968 | 323.159 | 0 | 0 | Bathroom x 4 | Fluorescente tube | 0 | 0 | 20 | 6 | 0 | 1656
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | Fluorescent lamp | 50% | 403 |  | Computer Lab | Fluorescente tube |  | 64 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 4006.1952 | 2003.0976 | 2003.0976 | 1034.1087 | 0 | 0 | Computer Lab | Fluorescente tube | 0 | 0 | 64 | 6 | 0 | 1656
#N/A | #N/A | #VALUE! | #N/A | Fluorescente tube | 50% |  |  | Storage x 2 | Fluorescente tube |  | 8 | 0 | 0 | 2 | 36 | 2 |  | 552 | 166.9248 | 83.4624 | 83.4624 | 43.0879 | 0 | 0 | Storage x 2 | Fluorescente tube | 0 | 0 | 8 | 2 | 0 | 552
|  |  |  | Fluorescente tube short | 50% |  |  | Hallway | LED lamp |  | 2 | 0 | 0 | 6 | 10 | 6 |  | 1656 | 33.12 | #N/A | #N/A | #N/A | #N/A | #N/A | Hallway | LED lamp | 0 | 0 | 2 | 6 | 0 | 1656
|  |  |  | PLL | 40% |  |  | Hallway | Fluorescent lamp |  | 3 | 0 | 0 | 6 | 15 | 6 |  | 1656 | 74.52 | 37.26 | 37.26 | 19.2357 | 403 | 1209 | Hallway | Fluorescent lamp | 0 | 0 | 3 | 6 | 0 | 1656
Lifespan (years) | 10 |  |  | T12 fluorscent tube | 80% |  |  | Staff room | Fluorescente tube |  | 8 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 500.7744 | 250.3872 | 250.3872 | 129.2636 | 0 | 0 | Staff room | Fluorescente tube | 0 | 0 | 8 | 6 | 0 | 1656
Year | USD |  |  | Halogen | 80% |  |  | Lecture Room | Fluorescente tube |  | 24 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 1502.3232 | 751.1616 | 751.1616 | 387.7908 | 0 | 0 | Lecture Room | Fluorescente tube | 0 | 0 | 24 | 6 | 0 | 1656
0 | #N/A |  |  | halogen projector lamp | 50% | 403 |  | Lecture Room | Fluorescente tube |  | 2 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 125.1936 | 62.5968 | 62.5968 | 32.3159 | 0 | 0 | Lecture Room | Fluorescente tube | 0 | 0 | 2 | 6 | 0 | 1656
1 | #N/A |  |  | Sodum (HPS) | 80% |  |  | Lecture room Nr2 | Fluorescente tube |  | 48 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 3004.6464 | 1502.3232 | 1502.3232 | 775.5815 | 0 | 0 | Lecture room Nr2 | Fluorescente tube | 0 | 0 | 48 | 6 | 0 | 1656
2 | #N/A |  |  | AR111 | 0% |  |  | Lecture room Nr2 | Fluorescente tube |  | 2 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 125.1936 | 62.5968 | 62.5968 | 32.3159 | 0 | 0 | Lecture room Nr2 | Fluorescente tube | 0 | 0 | 2 | 6 | 0 | 1656
3 | #N/A |  |  | LED (projector, otros) | 0% |  |  | Cafeteria | Fluorescente tube |  | 12 | 0 | 0 | 0 | 36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cafeteria | Fluorescente tube | 0 | 0 | 12 | 0 | 0 | 0
4 | #N/A |  |  | 0 | 0% |  |  | Lecture room nNr3 | Fluorescente tube |  | 40 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 2503.872 | 1251.936 | 1251.936 | 646.3179 | 0 | 0 | Lecture room nNr3 | Fluorescente tube | 0 | 0 | 40 | 6 | 0 | 1656
5 | #N/A | [6 empty] | Lecture room nNr3 | Fluorescente tube |  | 2 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 125.1936 | 62.5968 | 62.5968 | 32.3159 | 0 | 0 | Lecture room nNr3 | Fluorescente tube | 0 | 0 | 2 | 6 | 0 | 1656
6 | #N/A | [6 empty] | Lecture Room Nr4 | Fluorescente tube |  | 40 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 2503.872 | 1251.936 | 1251.936 | 646.3179 | 0 | 0 | Lecture Room Nr4 | Fluorescente tube | 0 | 0 | 40 | 6 | 0 | 1656
7 | #N/A | [6 empty] | Lecture Room Nr4 | Fluorescente tube |  | 2 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 125.1936 | 62.5968 | 62.5968 | 32.3159 | 0 | 0 | Lecture Room Nr4 | Fluorescente tube | 0 | 0 | 2 | 6 | 0 | 1656
8 | #N/A | [6 empty] | Theatre Nr2 | Fluorescente tube |  | 72 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 4506.9696 | 2253.4848 | 2253.4848 | 1163.3723 | 0 | 0 | Theatre Nr2 | Fluorescente tube | 0 | 0 | 72 | 6 | 0 | 1656
9 | #N/A | [6 empty] | Theatre Nr1 | Fluorescente tube |  | 128 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 8012.3904 | 4006.1952 | 4006.1952 | 2068.2174 | 0 | 0 | Theatre Nr1 | Fluorescente tube | 0 | 0 | 128 | 6 | 0 | 1656
10 | #N/A | [6 empty] | Theatre Nr1 | Fluorescent lamp |  | 8 | 0 | 0 | 6 | 15 | 6 |  | 1656 | 198.72 | 99.36 | 99.36 | 51.2951 | 403 | 3224 | Theatre Nr1 | Fluorescent lamp | 0 | 0 | 8 | 6 | 0 | 1656
[8 empty] | Theatre Nr3 | Fluorescente tube |  | 72 | 0 | 0 | 6 | 36 | 6 |  | 1656 | 4506.9696 | 2253.4848 | 2253.4848 | 1163.3723 | 0 | 0 | Theatre Nr3 | Fluorescente tube | 0 | 0 | 72 | 6 | 0 | 1656
[8 empty] | Exterior | Fluorescent lamp |  | 8 | 0 | 0 | 12 | 15 | 12 |  | 4368 | 524.16 | 262.08 | 262.08 | 135.3001 | 403 | 3224 | Exterior | Fluorescent lamp | 0 | 0 | 8 | 12 | 0 | 4368
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | Total |  | 32016 | 38454.1776 | #N/A | #N/A | #N/A |  | #N/A

## EEM2
|  |  |  | Lighting automation | [17 empty] | Mov. Sensor
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate | [18 empty] | Photocell
0.51625 | 10 | 6% | 2 | [12 empty] | Ahorros | [5 empty] | Central control
|  |  |  | Zone | Type | Nro_fixtures | Lamp_x_fix | Conumpion (kWh/year) | Control | Total (h/year) | % hours reduction | New hours (h/years) | Columna2 |  |  | Control type | Future (kWh/year) | Savings (kWh/year) | Savings (USD/año) | Quantity | Cost (USD) | None |  | Lugar | Tipo_Lamp | Nro_Lum | Lamp_x_Lum | Horas actuales (h/año) | Horas futuras (h/año) | Tipo de control | Cantidades de equipos | Consumo actual (kWh/año) | Consumo futuro (kWh/año)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (tonCO2/year) | Lobby | Lobby | 6 | 1 | 149.04 | 0 | 1656 | 0% | 1656 | Fluorescent lamp | 6 | 15 |  | 149.04 | 0 | 0 | 0 | 0 |  |  | Lobby | Lobby | 6 | 1 | 1656 | 1656 |  | 0 | 149.04 | 149.04
1063.5521 | 2060.1302 | 0.8421% | 1.3061 | Seminar roomx3 | Seminar roomx3 | 36 | 2 | 4506.9696 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 72 | 36 |  | 4506.9696 | 0 | 0 | 0 | 0 | Control | Unitary cost | Seminar roomx3 | Seminar roomx3 | 36 | 2 | 1656 | 1656 |  | 0 | 4506.9696 | 4506.9696
|  |  |  | Bathroom x 4 | Bathroom x 4 | 20 | 1 | 1251.936 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 20 | 36 |  | 1251.936 | 0 | 0 | 0 | 0 | Mov. Sensor | 33 | Bathroom x 4 | Bathroom x 4 | 20 | 1 | 1656 | 1656 |  | 0 | 1251.936 | 1251.936
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | Computer Lab | Computer Lab | 32 | 2 | 4006.1952 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 64 | 36 |  | 4006.1952 | 0 | 0 | 0 | 0 | Photocell | 26.6 | Computer Lab | Computer Lab | 32 | 2 | 1656 | 1656 |  | 0 | 4006.1952 | 4006.1952
0 | 0 | #NUM! | 7384.7508 | Storage x 2 | Storage x 2 | 4 | 2 | 166.9248 | 0 | 552 | 0% | 552 | Fluorescente tube | 8 | 36 |  | 166.9248 | 0 | 0 | 0 | 0 | None | 0 | Storage x 2 | Storage x 2 | 4 | 2 | 552 | 552 |  | 0 | 166.9248 | 166.9248
|  |  |  | Hallway | Hallway | 2 | 1 | 33.12 | 0 | 1656 | 30% | 1159.2 | LED lamp | 2 | 10 |  | 23.184 | 9.936 | 5.1295 | 0 | 0 | Central control | 100 | Hallway | Hallway | 2 | 1 | 1656 | 1159.2 |  | 0 | 33.12 | 23.184
|  |  |  | Hallway | Hallway | 3 | 1 | 74.52 | 0 | 1656 | 0% | 1656 | Fluorescent lamp | 3 | 15 |  | 74.52 | 0 | 0 | 0 | 0 |  |  | Hallway | Hallway | 3 | 1 | 1656 | 1656 |  | 0 | 74.52 | 74.52
|  |  |  | Staff room | Staff room | 4 | 2 | 500.7744 | 0 | 1656 | 30% | 1159.2 | Fluorescente tube | 8 | 36 |  | 350.5421 | 150.2323 | 77.5582 | 0 | 0 |  |  | Staff room | Staff room | 4 | 2 | 1656 | 1159.2 |  | 0 | 500.7744 | 350.5421
Lifespan (years) | 10 |  |  | Lecture Room | Lecture Room | 12 | 2 | 1502.3232 | 0 | 1656 | 30% | 1159.2 | Fluorescente tube | 24 | 36 |  | 1051.6262 | 450.697 | 232.6745 | 0 | 0 |  |  | Lecture Room | Lecture Room | 12 | 2 | 1656 | 1159.2 |  | 0 | 1502.3232 | 1051.6262
Year | USD |  |  | Lecture Room | Lecture Room | 2 | 1 | 125.1936 | 0 | 1656 | 30% | 1159.2 | Fluorescente tube | 2 | 36 |  | 87.6355 | 37.5581 | 19.3895 | 0 | 0 |  |  | Lecture Room | Lecture Room | 2 | 1 | 1656 | 1159.2 |  | 0 | 125.1936 | 87.6355
0 | 0 |  |  | Lecture room Nr2 | Lecture room Nr2 | 24 | 2 | 3004.6464 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 48 | 36 |  | 3004.6464 | 0 | 0 | 0 | 0 |  |  | Lecture room Nr2 | Lecture room Nr2 | 24 | 2 | 1656 | 1656 |  | 0 | 3004.6464 | 3004.6464
1 | 1063.5521 |  |  | Lecture room Nr2 | Lecture room Nr2 | 2 | 1 | 125.1936 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 2 | 36 |  | 125.1936 | 0 | 0 | 0 | 0 |  |  | Lecture room Nr2 | Lecture room Nr2 | 2 | 1 | 1656 | 1656 |  | 0 | 125.1936 | 125.1936
2 | 1063.5521 |  |  | Cafeteria | Cafeteria | 6 | 2 | 0 | 0 | 0 | 0% | 0 | Fluorescente tube | 12 | 36 |  | 0 | 0 | 0 | 0 | 0 |  |  | Cafeteria | Cafeteria | 6 | 2 | 0 | 0 |  | 0 | 0 | 0
3 | 1063.5521 |  |  | Lecture room nNr3 | Lecture room nNr3 | 20 | 2 | 2503.872 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 40 | 36 |  | 2503.872 | 0 | 0 | 0 | 0 |  |  | Lecture room nNr3 | Lecture room nNr3 | 20 | 2 | 1656 | 1656 |  | 0 | 2503.872 | 2503.872
4 | 1063.5521 |  |  | Lecture room nNr3 | Lecture room nNr3 | 2 | 1 | 125.1936 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 2 | 36 |  | 125.1936 | 0 | 0 | 0 | 0 |  |  | Lecture room nNr3 | Lecture room nNr3 | 2 | 1 | 1656 | 1656 |  | 0 | 125.1936 | 125.1936
5 | 1063.5521 |  |  | Lecture Room Nr4 | Lecture Room Nr4 | 20 | 2 | 2503.872 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 40 | 36 |  | 2503.872 | 0 | 0 | 0 | 0 |  |  | Lecture Room Nr4 | Lecture Room Nr4 | 20 | 2 | 1656 | 1656 |  | 0 | 2503.872 | 2503.872
6 | 1063.5521 |  |  | Lecture Room Nr4 | Lecture Room Nr4 | 2 | 1 | 125.1936 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 2 | 36 |  | 125.1936 | 0 | 0 | 0 | 0 |  |  | Lecture Room Nr4 | Lecture Room Nr4 | 2 | 1 | 1656 | 1656 |  | 0 | 125.1936 | 125.1936
7 | 1063.5521 |  |  | Theatre Nr2 | Theatre Nr2 | 36 | 2 | 4506.9696 | 0 | 1656 | 30% | 1159.2 | Fluorescente tube | 72 | 36 |  | 3154.8787 | 1352.0909 | 698.0234 | 0 | 0 |  |  | Theatre Nr2 | Theatre Nr2 | 36 | 2 | 1656 | 1159.2 |  | 0 | 4506.9696 | 3154.8787
8 | 1063.5521 |  |  | Theatre Nr1 | Theatre Nr1 | 64 | 2 | 8012.3904 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 128 | 36 |  | 8012.3904 | 0 | 0 | 0 | 0 |  |  | Theatre Nr1 | Theatre Nr1 | 64 | 2 | 1656 | 1656 |  | 0 | 8012.3904 | 8012.3904
9 | 1063.5521 |  |  | Theatre Nr1 | Theatre Nr1 | 8 | 1 | 198.72 | 0 | 1656 | 30% | 1159.2 | Fluorescent lamp | 8 | 15 |  | 139.104 | 59.616 | 30.777 | 0 | 0 |  |  | Theatre Nr1 | Theatre Nr1 | 8 | 1 | 1656 | 1159.2 |  | 0 | 198.72 | 139.104
10 | 1063.5521 |  |  | Theatre Nr3 | Theatre Nr3 | 36 | 2 | 4506.9696 | 0 | 1656 | 0% | 1656 | Fluorescente tube | 72 | 36 |  | 4506.9696 | 0 | 0 | 0 | 0 |  |  | Theatre Nr3 | Theatre Nr3 | 36 | 2 | 1656 | 1656 |  | 0 | 4506.9696 | 4506.9696
|  |  |  | Exterior | Exterior | 8 | 1 | 524.16 | 0 | 4368 | 0% | 4368 | Fluorescent lamp | 8 | 15 |  | 524.16 | 0 | 0 | 0 | 0 |  |  | Exterior | Exterior | 8 | 1 | 4368 | 4368 |  | 0 | 524.16 | 524.16
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 38454.1776 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 38454.1776 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[9 empty] | 0 | [7 empty] | 74848.225 | 2060.1302 | 1063.5521 |  | 0
Note on N4: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: se carga manual a partir de lo que cargue el auditor

## MCE3 (hidden)
Tuberías sin aislar
Vida útil (años) | Tasa de descuento | Tipo de cambio
10 | 10% | 2 | [18 empty] | Calculos | [12 empty] | 30mm | 50mm
[7 empty] | Tubería | Tipo de proceso | Equipo asociado | Combustible | Largo (m) | Diámetro (mm) | Rendimiento / COP | Temp ambiente (ºC) | Temperatura del tubo (ºC) | Espesor aislante (mm) | Horas funcionamiento al dia | Días a la semana | Semanas al año | Consumo anual (kWh/lt/m3/kg) | Diferencia de temp. (ªC) | Pérdidas térmicas (kW) | Nuevas pérdidas térmicas (kW) | Consumo anual (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) |  |  |  |  | Tubería (mm) | Costo unitario (USD/m) | Costo unitario (USD/m) | [9 empty] | Tubería | Equipo asociado | Largo (m) | Diámetro (mm) | Rendimiento / COP | Temp ambiente (ºC) | Temperatura del tubo (ºC) | Horas de uso (h/día) | Pérdidas térmicas (kW) | Consumo anual (kWh/año) | Tubería | Nuevas pérdidas térmicas (kW) | Nuevo Consumo Anual (kWh/año) | Ahorro (kWh/año)
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [11 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 20 |  |  |  | listas | [5 empty] | Monómicos |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | #DIV/0! | [11 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 25 |  |  |  | Electricidad |  | 1 | kWh/kWh | 0 | $/kWh | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 32 |  |  |  | Gas Natural |  | 9.6512 | kWh/m3 | 0 | $/m3 | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Vida útil de la medida | TIR | VAN | [6 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 40 | 8.18 | 15.99 |  | Gas oil |  | 10.093 | kWh/lt | 0 | $/lt | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10 | #NUM! | 0 | [6 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 50 |  |  |  | GLP |  | 12.6744 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 65 |  |  |  | Biomasa |  | 2.3372 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 80 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energía total Referencia |  |  | Energía total Medida | [6 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 100 |  |  |  | espesor aislante | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | kWh |  | 0 | kWh | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 150 |  |  |  | 30 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 |  |  |  |  | 0 | 0 | 0 |  | 50 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Descripción técnica: | [10 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [8 empty] | frío |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Año | USD |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [8 empty] | vapor |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [10 empty] | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 9 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 10 | 0 |  |  |  |  | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | DT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[30 empty] | Diferencia de temp (ºC) | 20 | 4 | 5 | 6 | 6.5 | 6 | 7 | 8 | 10 | 12 | 18
[31 empty] | 40 | 8 | 9 | 10 | 12 | 14 | 16 | 18 | 20 | 25 | 32
[31 empty] | 60 | 12 | 14 | 16 | 18 | 20 | 23 | 27 | 30 | 40 | 50
[31 empty] | 80 | 17 | 19 | 21 | 25 | 27 | 30 | 36 | 40 | 50 | 70
[31 empty] | 100 | 20 | 25 | 27 | 32 | 35 | 40 | 48 | 50 | 65 | 90
[31 empty] | 120 | 25 | 30 | 33 | 42 | 45 | 50 | 58 | 65 | 85 | 105
[31 empty] | 140 | 30 | 35 | 38 | 50 | 55 | 60 | 70 | 80 | 100
[31 empty] | 160 | 35 | 40 | 45 | 55 | 65 | 70 | 80 | 100
[31 empty] | 180 | 40 | 50 | 58 | 65 | 70 | 80 | 100
Pérdidas de calor (W/m)
[30 empty] | Diferencia de temperatura entre el tubo y el ambiente | Dimensión (mm)
[30 empty] | DT | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 150
[30 empty] | 35 | 27.2727 | 32.5455 | 38.9091 | 66.7273 | 54.5455 | 63.2727 | 72.9091 | 96.3636 | 112.7273
[30 empty] | 45 | 40 | 48 | 58 | 84 | 80 | 96 | 112 | 140 | 170
[29 empty] | Diferencia de temp (ºC) | 56 | 54 | 65 | 79 | 103 | 108 | 132 | 155 | 188 | 233
[30 empty] | 67 | 68 | 82 | 100 | 122 | 136 | 168 | 198 | 236 | 296
[30 empty] | 78 | 83 | 100 | 122 | 149 | 166 | 203 | 241 | 298 | 360
[30 empty] | 89 | 99 | 120 | 146 | 179 | 205 | 246 | 289 | 346 | 434
[30 empty] | 100 | 116 | 140 | 169 | 208 | 234 | 285 | 337 | 400 | 501
[30 empty] | 111 | 134 | 164 | 198 | 241 | 271 | 334 | 392 | 469 | 598
[30 empty] | 125 | 159 | 191 | 233 | 285 | 321 | 394 | 464 | 555 | 698
[30 empty] | 139 | 184 | 224 | 272 | 333 | 373 | 458 | 540 | 622 | 815
[30 empty] | 153 | 210 | 255 | 312 | 382 | 429 | 528 | 623 | 747 | 939
[30 empty] | 167 | 241 | 292 | 357 | 437 | 489 | 602 | 713 | 838 | 1093
[30 empty] | 180 | 274 | 329 | 408 | 494 | 556 | 676 | 808 | 959 | 1190
[30 empty] | 194 | 309 | 372 | 461 | 566 | 634 | 758 | 909 | 1080 | 1303
[40 empty] | 225 | 280
[40 empty] | 375 | 575
[40 empty] | 465 | 660
[40 empty] | 565 | 815
[40 empty] | 700 | 1000
[40 empty] | 790 | 1120
[40 empty] | 975 | 1390
[40 empty] | 1150 | 1650
[40 empty] | 1380 | 1980
[40 empty] | 1740 | 2520
[40 empty] | 2430 | 3500
[40 empty] | 3100 | 4430
[40 empty] | 3780 | 5600
[40 empty] | 4430 | 6450
Note on W5: fghiar: para ingresar manual
Note on AI59: Federico González Madina: interpolación
Note on AI60: Federico González Madina: interpolación

## MCE4 (hidden)
Tanque sin aislar
Vida útil (años) | Tasa de descuento | Tipo de cambio
0 | 10% | 2 | [19 empty] | Calculos
[7 empty] | Tanque | Tipo de proceso | Equipo asociado | Combustible | Alto (m) | Diámetro (m) | Área (m2) | Rendimiento / COP | Temp ambiente (ºC) | Temperatura sup (ºC) | Espesor aislante (mm) | Horas encedido al dia | Días de la semana | Semanas al año | Consumo anual (kWh/lt/m3/kg) | Diferencia de temp. (ªC) | Pérdidas top (kW) | Pérdidas sides (kW) | Pérdidas base (kW) | Pérdidas térmicas (kW) | Nuevas pérdidas térmicas (kW) | Consumo anual (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) |  | Aislación - Espesor (mm) | Costo unitario (USD/m2) | [11 empty] | Tanque | Equipo asociado | Alto (m) | Diámetro (m) | Rendimiento / COP | Temp ambiente (ºC) | Temperatura sup (ºC) | Horas de uso diarias | Pérdidas térmicas (kW) | Consumo anual (kWh/año) | Tanque | Espesor aislante (mm) | Nuevas pérdidas térmicas (kW) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año)
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 20 |  |  |  | listas | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | #DIV/0! | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 30 |  |  |  | Electricidad |  | 1 | kWh/kWh | 0 | $/kWh | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Gas Natural |  | 9.6512 | kWh/m3 | 0 | $/m3 | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Vida útil de la medida | TIR | VAN | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Gas oil |  | 10.093 | kWh/lt | 0 | $/lt | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | #NUM! | 0 | [8 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | GLP |  | 12.6744 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | Total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Biomasa |  | 2.3372 | kWh/kg | 0 | $/kg | 0 | $/kWh
| Energía total Referencia |  | Energía total Medida | [35 empty] | 0
| 0 | kWh | 0 | kWh
Descripción técnica:
[37 empty] | frío | 0 | 0 | 0 | 0
[5 empty] | Año | USD | [30 empty] | vapor | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0
[5 empty] | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0
[5 empty] | 2 | 0 | [31 empty] | 0 | 0 | 0
[5 empty] | 3 | 0 | [31 empty] | 0 | 0 | 0
[5 empty] | 4 | 0 | [31 empty] | 0 | 0 | 0
[5 empty] | 5 | 0 | [31 empty] | 0 | 0 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0
[5 empty] | 7 | 0
[5 empty] | 8 | 0
[5 empty] | 9 | 0
[5 empty] | 10 | 0
[33 empty] | DT | top | sides | base
[33 empty] | 30 | 14 | 10.5 | 7.5
[33 empty] | 50 | 15 | 11.5 | 8
[33 empty] | 70 | 16 | 12.5 | 8.5
[33 empty] | 90 | 17 | 13.5 | 9
[33 empty] | 110 | 18.3 | 14.5 | 9.5
[33 empty] | 130 | 19.5 | 15.5 | 10
[33 empty] | 150 | 21.5 | 16.5 | 11
[33 empty] | 170 | 23.5 | 17.9 | 12
[33 empty] | A | 0.0002 | 4e-05 | 0.0001
[33 empty] | B | 0.0183 | 0.0433 | 0.0083
[33 empty] | C | 13.386 | 9.2125 | 7.2537
[42 empty] | 225 | 280
[42 empty] | 375 | 575
[42 empty] | 465 | 660
[42 empty] | 565 | 815
[42 empty] | 700 | 1000
[42 empty] | 790 | 1120
[42 empty] | 975 | 1390
[42 empty] | 1150 | 1650
[42 empty] | 1380 | 1980
[42 empty] | 1740 | 2520
[42 empty] | 2430 | 3500
[42 empty] | 3100 | 4430
[42 empty] | 3780 | 5600
[42 empty] | 4430 | 6450
Note on X5: ingresar manualmente

## MCE5 (hidden)
Vida útil (años) | Tasa de descuento | Tipo de cambio
10 | 10% | 2 | [16 empty] | Calculos
[7 empty] | Horno | Combustible | Area (m2) | Posición | Rendimiento | Temp ambiente (ºC) | Temperatura sup (ºC) | Espesor aislante (mm) | Horas encedido al dia | Días de la semana | Semanas al año | Consumo anual (kWh/lt/m3/kg) | Diferencia de temp. (ªC) | Pérdidas térmicas (kW) | Nuevas pérdidas térmicas (kW) | Consumo anual (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) | Aislación - Espesor (mm) | Costo unitario (USD/m2) | [9 empty] | Horno | Combustible | Area (m2) | Rendimiento | Temp ambiente (ºC) | Temperatura sup (ºC) | Horas encedido al dia | Pérdidas térmicas (kW) | Consumo anual (kWh/año) | Horno | Espesor aislante (mm) | Nuevas pérdidas térmicas (kW) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año)
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 20 |  |  | listas | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 30 |  |  | Electricidad | 1 | kWh/kWh | 0 | $/kWh | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Gas Natural | 9.6512 | kWh/m3 | 0 | $/m3 | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Vida útil de la medida | TIR | VAN | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Gas oil | 10.093 | kWh/lt | 0 | $/lt | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10 | #NUM! | 0 | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | GLP | 12.6744 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Biomasa | 2.3372 | kWh/kg | 0 | $/kg | 0 | $/kWh
| Energía total Referencia |  | Energía total Medida
| 0 | kWh | 0 | kWh | [26 empty] | Superior
Lateral
Inferior
Descripción técnica:
[5 empty] | Año | USD
[5 empty] | 0 | 0 | [33 empty] | 25.4
[5 empty] | 1 | 0
[5 empty] | 2 | 0
[5 empty] | 3 | 0
[5 empty] | 4 | 0
[5 empty] | 5 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0
[5 empty] | 7 | 0
[5 empty] | 8 | 0
[5 empty] | 9 | 0
[5 empty] | 10 | 0
[28 empty] | Superior | Lateral | Inferior
[27 empty] | 30 | 14 | 10.5 | 7.5
[27 empty] | 50 | 15 | 11.5 | 8
[27 empty] | 70 | 16 | 12.5 | 8.5
[27 empty] | 90 | 17 | 13.5 | 9
[27 empty] | 110 | 18.3 | 14.5 | 9.5
[27 empty] | 130 | 19.5 | 15.5 | 10
[27 empty] | 150 | 21.5 | 16.5 | 11
[27 empty] | 170 | 23.5 | 17.9 | 12
[27 empty] | A | 0.0002 | 4e-05 | 0.0001
[27 empty] | B | 0.0183 | 0.0433 | 0.0083
[27 empty] | C | 13.386 | 9.2125 | 7.2537
[33 empty] | 225 | 280
[33 empty] | 375 | 575
[33 empty] | 465 | 660
[33 empty] | 565 | 815
[33 empty] | 700 | 1000
[33 empty] | 790 | 1120
[33 empty] | 975 | 1390
[33 empty] | 1150 | 1650
[33 empty] | 1380 | 1980
[33 empty] | 1740 | 2520
[33 empty] | 2430 | 3500
[33 empty] | 3100 | 4430
[33 empty] | 3780 | 5600
[33 empty] | 4430 | 6450
Note on R5: Agregar manualmente

## MCE6 (hidden)
Vida útil (años) | Tasa de descuento | Tipo de cambio
25 | 10% | 2 | [16 empty] | Calculos
[7 empty] | Cámara | Equipo asociado | Area (m2) | Posición | Rendimiento / COP | Temp ambiente (ºC) | Temperatura sup (ºC) | Espesor aislante (mm) | Horas encedido al dia | Días de la semana | Semanas al año | Consumo anual (kWh) | Diferencia de temp. (ªC) | Pérdidas térmicas (kW) | Nuevas pérdidas térmicas (kW) | Consumo anual (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) |  | Aislación - Espesor (mm) | Costo unitario (USD/m2) | [8 empty] | Cámara | Equipo asociado | Area (m2) | Posición | Rendimiento / COP | Temp ambiente (ºC) | Temperatura sup (ºC) | Horas encedido al dia | Pérdidas térmicas (kW) | Consumo anual (kWh/año) | Cámara | Espesor aislante (mm) | Nuevas pérdidas térmicas (kW) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año)
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [9 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 8.18 | listas | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | #DIV/0! | [9 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 15.99 | Electricidad |  | 1 | kWh/kWh | 0 | $/kWh | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Gas Natural |  | 9.6512 | kWh/m3 | 0 | $/m3 | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Vida útil de la medida | TIR | VAN | [10 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Gas oil |  | 10.093 | kWh/lt | 0 | $/lt | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 25 | #NUM! | 0 | [10 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Superior |  | GLP |  | 12.6744 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Lateral |  | Biomasa |  | 2.3372 | kWh/kg | 0 | $/kg | 0 | $/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energía total Referencia |  | Energía total Medida | [11 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | kWh | 0 | kWh | [10 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Superior | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Lateral | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Descripción técnica: | [14 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Año | $ | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 4 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 9 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 10 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Superior | Lateral | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 10.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 11.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 12.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 13.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18.3 | 14.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19.5 | 15.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 21.5 | 16.5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 23.5 | 17.9 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 0.0001 | 4e-05
[27 empty] | B | 0.0083 | 0.0433
[27 empty] | C | 7.2537 | 9.2125
[33 empty] | 225 | 280
[33 empty] | 375 | 575
[33 empty] | 465 | 660
[33 empty] | 565 | 815
[33 empty] | 700 | 1000
[33 empty] | 790 | 1120
[33 empty] | 975 | 1390
[33 empty] | 1150 | 1650
[33 empty] | 1380 | 1980
[33 empty] | 1740 | 2520
[33 empty] | 2430 | 3500
[33 empty] | 3100 | 4430
[33 empty] | 3780 | 5600
[33 empty] | 4430 | 6450
Note on T5: ingresar manualmente
Note on AG40: Federico González Madina: Estos valores son los de superficies inferiores dado que en este caso la diferencia de temperatura con el ambiente es al revés

## MCE7 (hidden)
INVENTARIO DE MOTORES ELÉCTRICOS INSTALADOS
Monómico ($/kWh) | Vida útil (años) | Tasa de descuento | Tipo de cambio
0 | 15 | 10% | 2
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) |  |  | Nombre del equipo | Marca/Modelo | Clase de motor | Cantidad (n°) | Potencia nominal (kW) | Potencia medida (kW) | Factor de pot. Medido | Uso diario (h/dia) | Variador frecuencia (SI/NO) | Frecuencia del VSD (Hz) | % en 25% | % en 50% | % en 75% | % mayor a 90% | Días/semna | Semanas/año | Uso total (h/año) | Observaciones | Eficiencia actual media(%) | Eficiencia futura media (%) | Pot_medida (kW) | Consumo total (kWh/año) | Nuevo consumo total (kWh/año) | Ahorro (kWh/año) | Ahorro ($) | Inversión (USD) | Nombre del equipo | Marca/Modelo | Clase de motor | Cantidad (n°) | Potencia nominal (kW) | Potencia medida (kW) | Factor de pot. Medido | Uso diario (h/dia) | Eficiencia actual media(%) | Consumo anual (kWh/año) | Nombre del equipo | Potencia nominal (kW) | Eficiencia futura media (%) | Nuevo consumo total (kWh/año) | Ahorro (kWh/año) | Nombre del equipo | Ahorro (USD/año) | Inversión (USD) | Payback (años)
0 | 0 | 0 |  | 0 | #DIV/0! | [18 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[24 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
|  | Vida útil (años) | TIR | VAN | [19 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
|  | 15 | #NUM! | 0 | [19 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[24 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Energía total Referencia |  | Energía total Medida | [20 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 0 | kWh | 0 | kWh | [19 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[24 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | Motores P(hp) | Costo unitario | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | Potencias | USD/KW | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Descripción técnica: |  |  |  |  | Mayores a 100 KW | 93.5065 | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | Entre 2 y 100 KW | 128.0315 | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | Menor 2KW | 368.1481 | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[24 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | Año | USD | [17 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[5 empty] | 0 | 0 | [21 empty] | Totales | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | 0
[5 empty] | 2 | 0
[5 empty] | 3 | 0
Recomendaciones técnicas: |  |  |  |  | 4 | 0
[5 empty] | 5 | 0
[5 empty] | 6 | 0
[5 empty] | 7 | 0
[5 empty] | 8 | 0
[5 empty] | 9 | 0
[5 empty] | 10 | 0
[5 empty] | 11 | 0
[5 empty] | 12 | 0
[5 empty] | 13 | 0
[5 empty] | 14 | 0
[5 empty] | 15 | 0
Note on D6: fghiar: depende qué motores involucre

## MCE8 (hidden)
INVENTARIO DE MOTORES ELÉCTRICOS INSTALADOS
Vida útil (años) | Tasa de descuento | Tipo de cambio
20 | 10% | 2
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) |  | Equipo | Energético | Unidades | Potencia térmica (kW) | Eficiencia (%) | Semanas al año | Consumo mensual (kWh/lt/m3/kg) | Nueva eficiencia (%) |  | Nuevo consumo total (kWh/lt/m3/kg) | Ahorro anual (kWh/lt/m3/kg) | Ahorro (kWh/año) | Ahorro ($) | Inversión (USD) | listas |  |  |  |  | Parámetros | O2 (%) | CO (ppm) | T chim (°C) | T amb (°C) | Eficiencia (%) | Eficiencia global (%)
0 | 0 | 0 |  | 0 | #DIV/0! | [15 empty] | Electricidad | 1 | kWh/kWh | 0 | $/kWh | Valores actuales promedio
[14 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | Gas Natural | 9.6512 | kWh/m3 | 0 | $/m3
|  | Vida útil de la medida | TIR | VAN | [9 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | Gas oil | 10.093 | kWh/lt | 0 | $/lt
|  | 20 | #NUM! | 0 | [9 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | GLP | 12.6744 | kWh/kg | 0 | $/kg
[14 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | Biomasa | 2.3372 | kWh/kg | 0 | $/kg
[14 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | 0
| Energía total Referencia |  | Energía total Medida | [10 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | [5 empty] | Parámetros | O2 (%) | CO (ppm) | T chim (°C) | T amb (°C) | Eficiencia (%) | Eficiencia global (%)
| 0 | kWh | 0 | kWh | [9 empty] | 0% |  | 0 | 0 | 0 | 0 | 0 | [5 empty] | Valores promedio sugeridos
[14 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Sistema de automatización - VSD y sensores | Costo unitario (USD/sistema) | [7 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
Descripción técnica: |  |  |  |  | 1 | 800 | [7 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[14 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[5 empty] | Año | USD | [7 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | [7 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | 0 | [7 empty] | 0% |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 2 | 0 | [8 empty] | Totales | 0 | 0 | 0 | 0 | 0
[5 empty] | 3 | 0
[5 empty] | 4 | 0
[5 empty] | 5 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0
[5 empty] | 7 | 0
[5 empty] | 8 | 0
[5 empty] | 9 | 0
[5 empty] | 10 | 0
Descripción de caldera/horno/otro:
Sistema de control a implementar (descripción)

## MCE10 (hidden)
MMEE 10. Reducción de presión en aire comprimido
Monómico ($/kWh) | Vida útil (años) | Tasa de descuento | Tipo de cambio
0 | 15 | 6% | 2
[7 empty] | Tipo de equipo | Uso | Foto | Equipo | Potencia (kW) | Presión seteo actual (bar) | Presión seteo futura (bar) | Variador de frecuencia | Consumo Anual (kWh/año) | Observaciones | Pot_térmica (kW) | Pot_inst (kW) | Reducción de (bar) | Consumo (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) | Reducción de potencia (%/bar) | Nombre del equipo | Potencia (kW) | Reducción de presión (bar) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año)
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [19 empty] | 0% | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | Tornillo | Distribuido | [8 empty] | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[7 empty] | Tornillo | Distribuido | [8 empty] | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Vida útil de la medida | TIR | VAN | [12 empty] | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
|  | 15 | #NUM! | 0 | [12 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
| Energía total Referencia |  | Energía total Medida | [13 empty] | #REF! | #REF!
| 0 | kWh | 0 | kWh | [12 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
Descripción técnica: | [16 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
[5 empty] | Año | USD | [10 empty] | #REF! | #REF!
[5 empty] | 0 | 0 | [10 empty] | #REF! | #REF!
[5 empty] | 1 | 0 | [10 empty] | #REF! | #REF!
[5 empty] | 2 | 0 | [10 empty] | #REF! | #REF!
[17 empty] | #REF! | #REF!
[15 empty] | 0 |  |  |  | Total | 0 | 0 | 0 | 0 | 0
Recomendaciones técnicas:

## MCE11 (hidden)
MMEE 11. Campaña de reducción de fugas
Monómico ($/kWh) | Vida útil (años) | Tasa de descuento | Tipo de cambio
0 | 25 | 6% | 2
[7 empty] | Cons. anual (kWh) | Pot_térmica (kW) | Pot_inst (kW) | Consumo Actual de pérdidas (%) | % Reducción de las pérdidas | Consumo (kWh/año) | Nuevo Consumo (kWh/año) | Ahorro (kWh/año) | Ahorro ($/año) | Inversión (USD) | Detección de fugas | Costo unitario
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) | [11 empty] | Campaña de detección
0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! |  | 0 | #REF! | #REF! | 20% | 0% | 0 | 0 | 0 | 0 |  | Materiales
[8 empty] | #REF! | #REF!
|  | Vida útil de la medida | TIR | VAN |  |  |  | #REF! | #REF!
|  | 25 | #NUM! | 0 |  |  |  | #REF! | #REF!
[8 empty] | #REF! | #REF!
| Energía total Referencia |  | Energía total Medida |  |  |  |  | #REF! | #REF!
| 0 | kWh | 0 | kWh |  |  |  | #REF! | #REF!
[8 empty] | #REF! | #REF!
[8 empty] | #REF! | #REF!
[8 empty] | #REF! | #REF!
Descripción técnica: | [7 empty] | #REF! | #REF!
[8 empty] | #REF! | #REF!
[5 empty] | Año | USD |  | #REF! | #REF!
[5 empty] | 0 | 0 |  | #REF! | #REF!
[5 empty] | 1 | 0 |  | #REF! | #REF!
[5 empty] | 2 | 0 |  | #REF! | #REF!
[8 empty] | #REF! | #REF!
[10 empty] | Total |  | 0 | 0 | 0 | 0 | 0
Recomendaciones técnicas:
Explicación de cómo se obtienen horas de funcionamiento:

## EEM3
Air conditioners automation
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 10 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New time of operation (%) | New consumption (kWh/year) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Control | Unitary cost (USD/split) | Zone | Brand/model | Quantity | Thermal power (BTU/h) | Consumption (kWh/year) | New time of operation (%) | Savings (kWh/año)
8288.2582 | 16054.5888 | 6.563% | 10.1786 | [24 empty] | Auto | 148 | Seminar room | Classic | 1 | 2.31 | 3060.288 | 70% | 918.0864
|  |  |  | 1 | Seminar room | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.31 | 3060.288 | 70% | 2142.2016 | 918.0864 | 473.9665 | 148 |  |  | Seminar room 2 | Classic | 1 | 2.31 | 3060.288 | 70% | 918.0864
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 2 | Seminar room 2 | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.31 | 3060.288 | 70% | 2142.2016 | 918.0864 | 473.9665 | 148 |  |  | Seminar room 3 | Daikin | 1 | 2.01 | 2662.848 | 70% | 798.8544
2664 | 0.32142 | 311.1% | 55036.1336 | 3 | Seminar room 3 | AC | Split | Daikin | 1 | 2.01 | 3.21 | 2.01 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.01 | 2662.848 | 70% | 1863.9936 | 798.8544 | 412.4124 | 148 |  |  | Computer Lab | MDV | 1 | 2.05 | 2715.84 | 70% | 814.752
|  |  |  | 4 | Computer Lab | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.05 | 2715.84 | 70% | 1901.088 | 814.752 | 420.6196 | 148 |  |  | Computer Lab | Delta | 1 | 2.18 | 2888.064 | 70% | 866.4192
|  |  |  | 5 | Computer Lab | AC | Split | Delta | 1 | 2.18 | 3.23 | 2.18 | 0 | 25 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.18 | 2888.064 | 70% | 2021.6448 | 866.4192 | 447.2931 | 148 |  |  | Computer Lab | Westinghouse | 1 | 1.89 | 2503.872 | 70% | 751.1616
Lifespan (years) | 10 |  |  | 6 | Computer Lab | AC | Split | Westinghouse | 1 | 1.89 | 2.79 | 1.89 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 1.89 | 2503.872 | 70% | 1752.7104 | 751.1616 | 387.7908 | 148 |  |  | Lecture Room | Lennox | 1 | 2.43 | 3219.264 | 70% | 965.7792
Year | USD |  |  | 7 | Lecture Room | AC | Split | Lennox | 1 | 2.43 | 2.89 | 2.43 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.43 | 3219.264 | 70% | 2253.4848 | 965.7792 | 498.5881 | 148 |  |  | Lecture Room | Midea | 1 | 2.43 | 3219.264 | 70% | 965.7792
0 | -2664 |  |  | 8 | Lecture Room | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.43 | 3219.264 | 70% | 2253.4848 | 965.7792 | 498.5881 | 148 |  |  | Lecture room Nr2 | Midea | 2 | 2.43 | 6438.528 | 70% | 1931.5584
1 | 8288.2582 |  |  | 9 | Lecture room Nr2 | AC | Split | Midea | 2 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 0.6 | 0 | 0 | 4.86 | 6438.528 | 70% | 4506.9696 | 1931.5584 | 997.1763 | 296 |  |  | Lecture room nNr3 | Daikin | 2 | 2.01 | 5325.696 | 70% | 1597.7088
2 | 8288.2582 |  |  | 10 | Lecture room nNr3 | AC | Split | Daikin | 2 | 2.01 | 3.21 | 2.01 | 0 | 25 | 8 | 6 | 46 | 0.6 | 0 | 0 | 4.02 | 5325.696 | 70% | 3727.9872 | 1597.7088 | 824.8248 | 296 |  |  | Lecture room nNr3 | MDV | 1 | 2.05 | 2715.84 | 70% | 814.752
3 | 8288.2582 |  |  | 11 | Lecture room nNr3 | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.05 | 2715.84 | 70% | 1901.088 | 814.752 | 420.6196 | 148 |  |  | Lecture room nNr3 | Streamline | 1 | 2.9 | 3841.92 | 70% | 1152.576
4 | 8288.2582 |  |  | 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 2.9 | 2.43 | 2.9 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.9 | 3841.92 | 70% | 2689.344 | 1152.576 | 595.0229 | 148 |  |  | Lecture Room Nr4 | TCL | 3 | 2.175 | 8644.32 | 70% | 2593.296
5 | 8288.2582 |  |  | 13 | Lecture Room Nr4 | AC | Split | TCL | 3 | 2.175 | 3.23 | 2.175 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 6.525 | 8644.32 | 70% | 6051.024 | 2593.296 | 1338.8014 | 444 |  |  | Lecture Room Nr4 | Midea | 1 | 2.43 | 3219.264 | 70% | 965.7792
6 | 8288.2582 |  |  | 14 | Lecture Room Nr4 | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.43 | 3219.264 | 70% | 2253.4848 | 965.7792 | 498.5881 | 148 |  |  | 0 | 0 | 0 | 0 | 0 | 100% | 0
7 | 8288.2582 |  |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 70% | 0
8 | 8288.2582 |  |  | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70% | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 70% | 0
9 | 8288.2582 |  |  | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70% | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 70% | 0
10 | 8288.2582 |  |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70% | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0
|  |  |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0
|  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 21 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 22 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 23 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 24 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 25 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 26 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 27 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  | 0 | 0% | 0
|  |  |  | 28 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | Total |  |  |  | 53515.296 | - | 16054.5888
[22 empty] | 53515.296 |  | 37460.7072 | 16054.5888 | 8288.2582 | 2664
Note on K11: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase
Note on K12: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase

## EEM4
Temperature adjustment
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | - | 6% | 2
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | Set point (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | Consumption (kWh/year) | New set point (ºC) | New Consumption (kWh/years) | Savings (kWh/year) | Savings (USD) | Cost (USD) | Savings percentage (%/ºC) | Zone | Brand/model | Quantity | Set point (ºC) | New set point (ºC) | Consumption (kWh/year) | Savings (kWh/year)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [18 empty] | Just for cooling |  |  |  | 3% | Seminar room | Classic | 1 | 21 | 21 | 3060.288 | 0
1028.0046 | 3982.5475 | 0.4202% | 2.5249 | 1 | Seminar room | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 3060.288 | 21 | 3060.288 | 0 | 0 | 0 |  | Seminar room 2 | Classic | 1 | 21 | 21 | 3060.288 | 0
|  |  |  | 2 | Seminar room 2 | AC | Split | Classic | 1 | 2.31 | 3.18 | 2.31 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 3060.288 | 21 | 3060.288 | 0 | 0 | 0 |  | Seminar room 3 | Daikin | 1 | 21 | 21 | 2662.848 | 0
Cost (USD) | Payback (years) | IRR (%) | NPV (USD) | 3 | Seminar room 3 | AC | Split | Daikin | 1 | 2.01 | 3.21 | 2.01 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 2662.848 | 21 | 2662.848 | 0 | 0 | 0 |  | Computer Lab | MDV | 1 | 24 | 21 | 2715.84 | 244.4256
0 | 0 | - | - | 4 | Computer Lab | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 2715.84 | 21 | 2471.4144 | 244.4256 | 126.1859 | 0 |  | Computer Lab | Delta | 1 | 25 | 21 | 2888.064 | 346.5677
|  |  |  | 5 | Computer Lab | AC | Split | Delta | 1 | 2.18 | 3.23 | 2.18 | 0 | 25 | 8 | 6 | 46 | 0.6 | 0 | 2888.064 | 21 | 2541.4963 | 346.5677 | 178.9172 | 0 |  | Computer Lab | Westinghouse | 1 | 24 | 21 | 2503.872 | 225.3485
|  |  |  | 6 | Computer Lab | AC | Split | Westinghouse | 1 | 1.89 | 2.79 | 1.89 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 2503.872 | 21 | 2278.5235 | 225.3485 | 116.3372 | 0 |  | Lecture Room | Lennox | 1 | 24 | 21 | 3219.264 | 289.7338
|  |  |  | 7 | Lecture Room | AC | Split | Lennox | 1 | 2.43 | 2.89 | 2.43 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 3219.264 | 21 | 2929.5302 | 289.7338 | 149.5764 | 0 |  | Lecture Room | Midea | 1 | 23 | 21 | 3219.264 | 193.1558
|  |  |  | 8 | Lecture Room | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 0.6 | 0 | 3219.264 | 21 | 3026.1082 | 193.1558 | 99.7176 | 0 |  | Lecture room Nr2 | Midea | 2 | 23 | 21 | 6438.528 | 386.3117
Año | USD |  |  | 9 | Lecture room Nr2 | AC | Split | Midea | 2 | 2.43 | 2.93 | 2.43 | 0 | 23 | 8 | 6 | 46 | 0.6 | 0 | 6438.528 | 21 | 6052.2163 | 386.3117 | 199.4353 | 0 |  | Lecture room nNr3 | Daikin | 2 | 25 | 21 | 5325.696 | 639.0835
0 | 0 |  |  | 10 | Lecture room nNr3 | AC | Split | Daikin | 2 | 2.01 | 3.21 | 2.01 | 0 | 25 | 8 | 6 | 46 | 0.6 | 0 | 5325.696 | 21 | 4686.6125 | 639.0835 | 329.9299 | 0 |  | Lecture room nNr3 | MDV | 1 | 24 | 21 | 2715.84 | 244.4256
1 | 1028.0046 |  |  | 11 | Lecture room nNr3 | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 2715.84 | 21 | 2471.4144 | 244.4256 | 126.1859 | 0 |  | Lecture room nNr3 | Streamline | 1 | 24 | 21 | 3841.92 | 345.7728
2 | 1028.0046 |  |  | 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 2.9 | 2.43 | 2.9 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 3841.92 | 21 | 3496.1472 | 345.7728 | 178.5069 | 0 |  | Lecture Room Nr4 | TCL | 3 | 24 | 21 | 8644.32 | 777.9888
3 | 1028.0046 |  |  | 13 | Lecture Room Nr4 | AC | Split | TCL | 3 | 2.175 | 3.23 | 2.175 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 8644.32 | 21 | 7866.3312 | 777.9888 | 401.6404 | 0 |  | Lecture Room Nr4 | Midea | 1 | 24 | 21 | 3219.264 | 289.7338
4 | 1028.0046 |  |  | 14 | Lecture Room Nr4 | AC | Split | Midea | 1 | 2.43 | 2.93 | 2.43 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 3219.264 | 21 | 2929.5302 | 289.7338 | 149.5764 | 0 |  | Theatre Nr2 | Carrier | 1 | 0 | 21 | 19297.5753 | 0
5 | 1028.0046 |  |  | 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 19297.5753 | 21 | 19297.5753 | 0 | 0 | 0 |  | Theatre Nr3 (big) | Trane Oddissey | 2 | 0 | 21 | 61405.2116 | 0
6 | 1028.0046 |  |  | 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 23.1753 | 3 | 23.1753 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 61405.2116 | 21 | 61405.2116 | 0 | 0 | 0 |  | Theatre Nr1 | Carrier | 1 | 0 | 21 | 19297.5753 | 0
7 | 1028.0046 |  |  | 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 19297.5753 | 21 | 19297.5753 | 0 | 0 | 0 |  | Theatre Nr3 (big) | Trane Oddissey | 2 | 0 | 21 | 9869.76 | 0
8 | 1028.0046 |  |  | 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 9869.76 | 21 | 9869.76 | 0 | 0 | 0 |  | Theatre Nr1 | 0 | 1 | 0 | 0 | 4934.88 | 0
9 | 1028.0046 |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 4934.88 |  | 4934.88 | 0 | 0 | 0 |  | Theatre Nr2 | 0 | 1 | 0 | 0 | 4934.88 | 0
10 | 1028.0046 |  |  | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 4934.88 |  | 4934.88 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 21 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 22 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | Total |  |  |  |  | 72812.8713 | 3982.5475
[20 empty] | 72812.8713 |  | 169272.6306 | 3982.5475 | 2056.0092 | 0

## EEM5
Smart thermostats for central AC
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 10 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | Operation time reduction (%) | New consumption (kWh/year) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Control | Unitary cost (USD/unit)
509.5311 | 986.976 | 0.4034% | 0.62574 | [24 empty] | Smar thermostats | 269
|  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | Unit per Air handler
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
1883 | 3.6956 | 23.88% | 1761.5029 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Lifespan (years) | 10 |  |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Year | USD |  |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
0 | -1883 |  |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
1 | 509.5311 |  |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
2 | 509.5311 |  |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
3 | 509.5311 |  |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
4 | 509.5311 |  |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
5 | 509.5311 |  |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
6 | 509.5311 |  |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
7 | 509.5311 |  |  | 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 14.5664 | 19297.5753 |  | 19297.5753 | 0 | 0 | 269
8 | 509.5311 |  |  | 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 23.1753 | 3 | 23.1753 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 46.3506 | 61405.2116 |  | 61405.2116 | 0 | 0 | 538
9 | 509.5311 |  |  | 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 14.5664 | 3 | 14.5664 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 14.5664 | 19297.5753 |  | 19297.5753 | 0 | 0 | 269
10 | 509.5311 |  |  | 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 7.45 | 9869.76 |  | 9869.76 | 0 | 0 | 538
|  |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 3.725 | 4934.88 | 10% | 4441.392 | 493.488 | 254.7655
|  |  |  | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 3.725 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 3.725 | 4934.88 | 10% | 4441.392 | 493.488 | 254.7655 | 269
|  |  |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  |  |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
[22 empty] | 119739.8821 |  | 118752.9061 | 986.976 | 509.5311 | 1883
Note on K11: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase
Note on K12: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase

## EEM6
Insulate air conditioning zones
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 10 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | Savings (%) | New consumption (kWh/year) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Cost of walls and windows adjusment | Specific repairs and adjusments have to be assess for each building
833.032 | 1613.6064 | 0.6596% | 1.023 | [24 empty] | 3000
[24 empty] | 0 | 0 | 0 | 0
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | [20 empty] | 0 | 0 | 0 | 0
6000 | 7.2026 | 6.459% | 123.7624 | 3 | Seminar room 3 | AC | Split | Daikin | 1 | 2.01 | 3.21 | 2.01 | 0 | 21 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.01 | 2662.848 | 30% | 1863.9936 | 798.8544 | 412.4124 | 3000
|  |  |  | 4 | Computer Lab | AC | Split | MDV | 1 | 2.05 | 3 | 2.05 | 0 | 24 | 8 | 6 | 46 | 0.6 | 0 | 0 | 2.05 | 2715.84 | 30% | 1901.088 | 814.752 | 420.6196 | 3000
[24 empty] | 0 | 0 | 0 | 0
Lifespan (years) | 25 | [22 empty] | 0 | 0 | 0 | 0
Year | USD | [22 empty] | 0 | 0 | 0 | 0
0 | -6000 | [22 empty] | 0 | 0 | 0 | 0
1 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
2 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
3 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
4 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
5 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
6 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
7 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
8 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
9 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
10 | 833.032 | [22 empty] | 0 | 0 | 0 | 0
11 | 833.032 |  |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
12 | 833.032 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
13 | 833.032 |  |  | 21 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
14 | 833.032 |  |  | 22 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
15 | 833.032 |  |  | 23 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
16 | 833.032 |  |  | 24 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
17 | 833.032 |  |  | 25 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
18 | 833.032 |  |  | 26 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
19 | 833.032 |  |  | 27 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
20 | 833.032 |  |  | 28 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
21 | 833.032 | [20 empty] | 5378.688 |  | 3765.0816 | 1613.6064 | 833.032 | 6000
22 | 833.032
23 | 833.032
24 | 833.032
25 | 833.032
Note on K11: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase
Note on K12: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Uso dos sensores por clase

## EEM7
Split air conditioners replacement
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) |  | All equipment | [33 empty] | LISTAS
10288.9825 | 19930.048 | 8.147% | 12.6357 | [35 empty] | Interior
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New COP | New thermal power (BTU/h) | Consumption (kWh/year ) | Inverter % savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | payback individual | Investments | [6 empty] | Exterior
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 1 | Seminar room | AC | Split | Classic | 1 | 7882.0472 | 3.18 | 2.31 | [10 empty] | 3.25 | 12000 | 3060.288 | 2.154% | 2994.3741 | 65.9139 | 34.0284 | 1204.9259 | 35.4095 | Inverter Air conditioners | XCD | USD | Installation | Capacity (BTU/h) | EER | Total investment (USD)
15276.36 | 1.4847 | 67.3% | 75810.912 | 2 | Seminar room 2 | AC | Split | Classic | 1 | 7882.0472 | 3.18 | 2.31 | [10 empty] | 3.25 | 12000 | 3060.288 | 2.154% | 2994.3741 | 65.9139 | 34.0284 | 1204.9259 | 35.4095 | Inverter 9,000 BTU/h |  | 850 | 150 | 9000 | 3.6 | 1204.9259 | Freezer
|  |  |  | 3 | Seminar room 3 | AC | Split | Daikin | 1 | 6858.4047 | 3.21 | 2.01 | [10 empty] | 3.25 | 12000 | 2662.848 | 1.231% | 2630.0745 | 32.7735 | 16.9195 | 1204.9259 | 71.2153 | Inverter 12,000 BTU/h | 2249 | 1054.9259 | 150 | 12000 | 3.25 | 1204.9259
|  |  |  | 4 | Computer Lab | AC | Split | MDV | 1 | 6994.8904 | 3 | 2.05 | [10 empty] | 3.25 | 12000 | 2715.84 | 7.692% | 2506.9292 | 208.9108 | 107.8512 | 1204.9259 | 11.1721 | Inverter 18,000 BTU/h | 2990 | 1387.037 | 150 | 18000 | 3.2 | 1537.037 | #REF!
|  |  |  | 5 | Computer Lab | AC | Split | Delta | 1 | 7438.4688 | 3.23 | 2.18 | [10 empty] | 3.25 | 12000 | 2888.064 | 0.6154% | 2870.2913 | 17.7727 | 9.1752 | 1204.9259 | 131.3236 | Inverter 24,000 BTU/h | 3899 | 1837.9185 | 150 | 24000 | 3.4 | 1987.9185 | #REF!
Lifespan (years) | 15 |  |  | 6 | Computer Lab | AC | Split | Westinghouse | 1 | 6448.9477 | 2.79 | 1.89 | [10 empty] | 3.25 | 12000 | 2503.872 | 14.15% | 2149.4778 | 354.3942 | 182.9577 | 1204.9259 | 6.5858 | Inverter 36,000 BTU/h | 7018.218 | 2599.34 | 150 | 36000 | 3.3 | 2749.34 | #REF!
Year | USD |  |  | 7 | Lecture Room | AC | Split | Lennox | 1 | 8291.5042 | 2.89 | 2.43 | [10 empty] | 3.25 | 12000 | 3219.264 | 11.08% | 2862.6686 | 356.5954 | 184.0941 | 1204.9259 | 6.5452 | [7 empty] | Refrigeración
0 | -15276.36 |  |  | 8 | Lecture Room | AC | Split | Midea | 1 | 8291.5042 | 2.93 | 2.43 | [10 empty] | 3.25 | 12000 | 3219.264 | 9.846% | 2902.2903 | 316.9737 | 163.6392 | 1204.9259 | 7.3633 | [7 empty] | Frío de proceso
1 | 10288.9825 |  |  | 9 | Lecture room Nr2 | AC | Split | Midea | 2 | 8291.5042 | 2.93 | 2.43 | [10 empty] | 3.25 | 12000 | 6438.528 | 9.846% | 5804.5806 | 633.9474 | 327.2784 | 2409.8519 | 7.3633 | [7 empty] | Frío acond. termico
2 | 10288.9825 |  |  | 10 | Lecture room nNr3 | AC | Split | Daikin | 2 | 6858.4047 | 3.21 | 2.01 | [10 empty] | 3.25 | 12000 | 5325.696 | 1.231% | 5260.149 | 65.547 | 33.839 | 2409.8519 | 71.2153
3 | 10288.9825 |  |  | 11 | Lecture room nNr3 | AC | Split | MDV | 1 | 6994.8904 | 3 | 2.05 | [10 empty] | 3.25 | 12000 | 2715.84 | 7.692% | 2506.9292 | 208.9108 | 107.8512 | 1204.9259 | 11.1721
4 | 10288.9825 |  |  | 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 9895.2107 | 2.43 | 2.9 | [10 empty] | 3.25 | 12000 | 3841.92 | 25.23% | 2872.574 | 969.346 | 500.4295 | 1204.9259 | 2.4078
6 | 10288.9825 |  |  | 13 | Lecture Room Nr4 | AC | Split | TCL | 3 | 7421.4081 | 3.23 | 2.175 | [10 empty] | 3.25 | 12000 | 8644.32 | 0.6154% | 8591.1242 | 53.1958 | 27.4626 | 3614.7778 | 131.6255
7 | 10288.9825 |  |  | 14 | Lecture Room Nr4 | AC | Split | Midea | 1 | 8291.5042 | 2.93 | 2.43 | [10 empty] | 3.25 | 12000 | 3219.264 | 9.846% | 2902.2903 | 316.9737 | 163.6392 | 1204.9259 | 7.3633
8 | 10288.9825 |  |  | 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | [10 empty] | 3.3 | 54000 | 19297.5753 | 9.091% | 17543.2503 | 1754.325 | 905.6787 | 2749.34 | 3.0357
9 | 10288.9825 |  |  | 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 79077.3245 | 3 | 23.1753 | [10 empty] | 3.3 | 84000 | 61405.2116 | 9.091% | 55822.9196 | 5582.292 | 2881.8849 | 5498.68 | 1.908
10 | 10288.9825 |  |  | 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | [10 empty] | 3.3 | 54000 | 19297.5753 | 9.091% | 17543.2503 | 1754.325 | 905.6787 | 2749.34 | 3.0357
11 | 10288.9825 |  |  | 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 12710.2276 | 0 | 3.725 | [10 empty] | 3.2 | 18000 | 9869.76 | 100% | 0 | 9869.76 | 5095.3107 | 3074.0741 | 0.60331
12 | 10288.9825 |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | [10 empty] | 3.2 | 18000
13 | 10288.9825 |  |  | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | [10 empty] | 3.2 | 18000
14 | 10288.9825
15 | 10288.9825
[25 empty] | 163385.4181 |  | 140757.5474 | 22627.8707 | 11681.7463 | 35760.1007 | 3.0612
26
[5 empty] | Equipment selected for retrofit payback less than: |  |  | 6 | years
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New COP | New thermal power (BTU/h) | Consumption (kWh/year ) | Inverter % savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | payback
|  |  |  | 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 9895.2107 | 2.43 | 2.9 | [10 empty] | 3.25 | 12000 | 3841.92 | 25.23% | 2872.574 | 969.346 | 500.4295 | 1204.9259 | 2.4078
|  |  |  | 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | [10 empty] | 3.3 | 54000 | 19297.5753 | 9.091% | 17543.2503 | 1754.325 | 905.6787 | 2749.34 | 3.0357
|  |  |  | 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 79077.3245 | 3 | 23.1753 | [10 empty] | 3.3 | 84000 | 61405.2116 | 9.091% | 55822.9196 | 5582.292 | 2881.8849 | 5498.68 | 1.908
|  |  |  | 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | [10 empty] | 3.3 | 54000 | 19297.5753 | 9.091% | 17543.2503 | 1754.325 | 905.6787 | 2749.34 | 3.0357
|  |  |  | 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 12710.2276 | 0 | 3.725 | [10 empty] | 3.2 | 18000 | 9869.76 | 100% | 0 | 9869.76 | 5095.3107 | 3074.0741 | 0.60331
[9 empty] | 7 | [15 empty] | 113712.0421 |  | 93781.9942 | 19930.048 | 10288.9825 | 15276.36 | 1.4847
Note on AS8: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Gree livo gen 3

## EEM8
Split air conditioners replacement
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) |  | All equipment | [33 empty] | LISTAS
#N/A | #N/A | #N/A | #N/A | [35 empty] | Interior
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New COP | New thermal power (BTU/h) | Consumption (kWh/year ) | Inverter % savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | payback individual | Investments | [6 empty] | Exterior
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | [28 empty] | Inverter Air conditioners | XCD | USD | Installation | Capacity (BTU/h) | EER | Total investment (USD)
#N/A | #N/A | #VALUE! | #N/A | [28 empty] | ELS240S4DS | Lennox |  |  | 234000 | 3 | 28000 | Freezer
[32 empty] | ELS150S4DS | Lennox |  |  | 150000 | 3.3 | 21000
|  |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18000 | 4934.88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [7 empty] | #REF!
|  |  |  | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | [10 empty] | #N/A | 18000 | [14 empty] | #REF!
Lifespan (years) | 15 |  |  | 6 | [34 empty] | #REF!
Year | USD |  |  | 7 | [34 empty] | Refrigeración
0 | #N/A |  |  | 8 | [34 empty] | Frío de proceso
1 | #N/A |  |  | 9 | [34 empty] | Frío acond. termico
2 | #N/A |  |  | 10
3 | #N/A |  |  | 11
4 | #N/A |  |  | 12
6 | #N/A |  |  | 13
7 | #N/A |  |  | 14
8 | #N/A |  |  | 15
9 | #N/A |  |  | 16
10 | #N/A |  |  | 17
11 | #N/A |  |  | 18
12 | #N/A |  |  | 19
13 | #N/A |  |  | 20
14 | #N/A |  |  | 21
15 | #N/A
[25 empty] | 4934.88 |  | #N/A | #N/A | #N/A | #N/A | #N/A
2
[5 empty] | Equipment selected for retrofit payback less than: |  |  | 8 | years
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New COP | New thermal power (BTU/h) | Consumption (kWh/year ) | Inverter % savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | payback
|  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[9 empty] | #N/A | [15 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A
Note on AS8: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Gree livo gen 3

## EEM9
Return air adjustment
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 20 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | [10 empty] | Consumption (kWh/year ) | Exterior air adjustment (%) | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Unitary cost (USD) - Damper | LISTAS
1019.0621 | 1973.952 | 0.8069% | 1.2515 | [25 empty] | 910 | Interior
|  |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 3.725 | 4934.88 | 4934.88 | -20% | 3947.904 | 986.976 | 509.5311 | 0 |  | Exterior
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | 0 | 0 | 8 | 6 | 46 | 0.6 | 0 | 0 | 3.725 | 4934.88 | 4934.88 | -20% | 3947.904 | 986.976 | 509.5311 | 910
910 | 0.89298 | 112% | 9868.6926 | [26 empty] | Freezer
#REF!
#REF!
Lifespan (years) | 20 | [28 empty] | #REF!
Year | USD | [28 empty] | Refrigeración
0 | -910 | [28 empty] | Frío de proceso
1 | 1019.0621 | [28 empty] | Frío acond. termico
2 | 1019.0621
3 | 1019.0621
4 | 1019.0621
6 | 1019.0621
7 | 1019.0621
8 | 1019.0621
9 | 1019.0621
10 | 1019.0621
11 | 1019.0621
12 | 1019.0621
13 | 1019.0621
14 | 1019.0621
15 | 1019.0621
16 | 1019.0621
17 | 1019.0621
18 | 1019.0621
19 | 1019.0621
20 | 1019.0621
[23 empty] | 9869.76 | -0.4 | 7895.808 | 1973.952 | 1019.0621 | 910
1
Note on AQ8: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Gree livo gen 3

## EEM10
Air curtains for cold rooms
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2
|  |  |  | System | Brand/model | Type | Quantity | Thermal power (kW) | Power (kW) | COP | Temperature (ºC) | Temp Set point (ºC) | VSD | Freq VSD | % time in load | Hours/day | Days/week | Weeks/year | Comments | 0 | Thermal_P (kW) | Electric_P (kW) | Consumption (kWh/year) | Infiltrations consumption (kWh/year) | Infiltrations savings (kWh/year) | Air cortaings consumption (kWh/year) | New consumption (kWh/año) | Savings (kWh/year) | Savings (USD) | Cost (USD)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [27 empty] | Hypotesis |  | Reference
0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Infiltrations consumption | 10% | Energy Efficiency Improvement and Cost Saving Opportunities for the Fruit and Vegetable Processing Industry
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Open hours/day | 1
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Air cortain power (kw) | 0.35
0 | #DIV/0! | #NUM! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Infiltrations reduction | 80%
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cost (1.2 m) | 1000
Lifespan (years) | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Año | USD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | https://grenada.desertcart.com/brand/air%20curtain
3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | https://grenada.desertcart.com/products/17394259
4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Awoco 48" Super Power 2 Speeds 1650CFM
5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cost (XCD) | 2089
6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Taxes (XCD) | 454
7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shipping (XCD) | 321
8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Installation (XCD) | 417.8
9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total (XCD) | 3281.8
10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total (USD) | 1640.9
11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0

## EEM11
Doors insulation improvement
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2
|  |  |  | System | Brand/model | Type | Quantity | Thermal power (kW) | Power (kW) | COP | Temperature (ºC) | Temp Set point (ºC) | VSD | Freq VSD | % time in load | Hours/day | Days/week | Weeks/year | Comments | 0 | Thermal_P (kW) | Electric_P (kW) | Consumption (kWh/year) | Infiltrations consumption (kWh/year) | Infiltrations savings (kWh/year) | Air cortaings consumption (kWh/year) | New consumption (kWh/año) | Savings (kWh/year) | Savings (USD) | Cost (USD)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [27 empty] | Hypotesis |  | Reference
0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Extra consuimption due to deficient door insulation infiltrations |  | Energy Efficiency Improvement and Cost Saving Opportunities for the Fruit and Vegetable Processing Industry
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8%
0 | #DIV/0! | #NUM! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cost USD
Lifespan (years) | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500
Año | USD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0

## EEM12
Freezer replacement
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2 | [23 empty] | Select
|  |  |  | System | Brand/model | Type | Quantity | Thermal power (kW) | Power (kW) | COP | Temperature (ºC) | Temp Set point (ºC) | VSD | Freq VSD | % time in load | Hours/day | Days/week | Weeks/year | Comments | 0 | Thermal_P (kW) | Electric_P (kW) | Consumption (kWh/year) | Infiltrations consumption (kWh/year) | Infiltrations savings (kWh/year) | Air cortaings consumption (kWh/year) | Poor condition (Yes/No) | Old equipment (yes/no) | New Consumption (kWh/year) | Savings (kWh/year) | Savings (USD) | Cost (USD) | Hypotesis |  | Reference
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [29 empty] | Savings |  | Energy Efficiency Improvement and Cost Saving Opportunities for the Fruit and Vegetable Processing Industry
247.8023 | 480 | 0.1962% | 0.30432 | Fridges | 0 | Small | 1 | 0 | 0.3 | 0 | 5 | 7 | 0 | 0 | 0.3 | 24 | 7 | 52 | 0 | 0 | 0 | 0.3 | 1200 | 240 | #REF! | 0 | Yes | Yes | 720 | 480 | 247.8023 | 1500 | Poor condition | 20%
|  |  |  | Freezer | 0 | Horizontal 2 door freezer | 3 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.3 | 24 | 7 | 52 | 0 | 0 | 0 | 1.5 | 5400 | 1080 | #REF! | 0 |  |  | 5400 | 0 | 0 | 0 | New technology | 20% |  | Yes
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | No
1500 | 6.0532 | 14.29% | 174.9764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
Lifespan (years) | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
Año | USD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0
0 | -1500 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
1 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
2 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
3 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
4 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0 | Freezer horizontal de 2 doors
5 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0 | 600 liters
6 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0 | Total (USD) | 1500 | https://grenada.desertcart.com/products/396296826-star-track-chest-freezer-520-liters-double-door-white-anti-scratch-cabinet-1-year-warranty-st-cfw-600-l
7 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
8 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
9 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
10 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
11 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
12 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
13 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
14 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
15 | 247.8023 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[24 empty] | 1320 | #REF! | 0 |  |  |  | 480 | 247.8023 | 1500

## EEM13
VSD compressed air
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 10 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | Device | Usage | Foto | Nominal Power (kW) | Set pressure (bar) | VSD | Hours/day | Days/week | Week/year | % on load | % on discharge | Power on load (kW) | Power on discharge (kW) | Consumption (kWh/year) | Observation |  | Pot_inst (kW) | Consumption (kWh/year) | VSD savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Cost
0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 2250 |  | USD | import,shipping installation | TOTAL (USD)
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 0 | VSD | 1500 | 750 | 2250
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 0
2250 | #DIV/0! | #NUM! | -2122.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 0 |  |  |  |  | https://www.usaircompressor.com/product-page/us5-d-series
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 0 |  |  |  |  | https://www.grainger.com/product/16V889?cm_mmc=PPC:Google-_-GlobalExport-_-UY-_-Acquisition-_-2022007&gclid=CjwKCAiAioifBhAXEiwApzCzttNe-FJs5AhmQhuRpEX59an9Ltz-dANqhDLBAKAvz7loPCOYMzk6eBoCF0MQAvD_BwE
Lifespan (years) | 10 | [17 empty] | Total |  | 0 |  | 0 | 0 | 0 | 2250
Año | USD | [23 empty] | Refrigeración
0 | -2250 | [23 empty] | Frío de proceso
1 | 0 | [23 empty] | Frío acond. termico
2 | 0
3 | 0 | [23 empty] | Si
4 | 0 | [23 empty] | No
6 | 0
7 | 0
8 | 0
9 | 0
10 | 0

## EEM14
VSD fans
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 10 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | Identification | Model/branch | Use | Type | Quantity | Power (kW) | Power meassured (W) | VSD (Yes/No) | Frequency VSD (Hz) | Use (h/day) | % time load | Days/week | Weeks/year | Total (h/year) | Notes |  | Pot_inst (kW) | Consumption (kWh/año) | VSD savings | New Consumption (kWh/year ) | Savings (kWh/year) | Savings (USD/year) | Cost (USD) | Cost
0 | 0 | 0% | 0 | Pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25% | 0 | 0 | 0 | 500 |  | USD | import,shipping installation | TOTAL (USD)
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | VSD | 1500 | 750 | 500
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | VSD | 1500 | 750 | 2250
500 | #DIV/0! | #NUM! | -471.6981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  |  |  |  | https://www.usaircompressor.com/product-page/us5-d-series
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 |  |  |  |  | https://www.grainger.com/product/16V889?cm_mmc=PPC:Google-_-GlobalExport-_-UY-_-Acquisition-_-2022007&gclid=CjwKCAiAioifBhAXEiwApzCzttNe-FJs5AhmQhuRpEX59an9Ltz-dANqhDLBAKAvz7loPCOYMzk6eBoCF0MQAvD_BwE
Lifespan (years) | 10 | [17 empty] | Total |  | 0 |  | 0 | 0 | 0 | 500
Año | USD | [23 empty] | Refrigeración
0 | -500 | [23 empty] | Frío de proceso
1 | 0 | [23 empty] | Frío acond. termico
2 | 0
3 | 0 | [23 empty] | Si
4 | 0 | [23 empty] | No
6 | 0
7 | 0
8 | 0
9 | 0
10 | 0

## EEM15
Water pumps replacement and VSD
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 20 | 6% | 2
|  |  |  | Identification | Model/branch | Use | Type | Quantity | Energetic | Power (kW) | Power meassured (kW) | VSD (Yes/No) | Frequency VSD (Hz) | Use (h/day) | % time load | Days/week | Monthly (kWh) | Weeks/year | Total (h/year) | Notes | Power_inst (kW) | Consumption (kWh/year) | Savings (%) | Savings (kWh/year) | Savings (USD/year) | Cost (USD)
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [23 empty] | LISTAS
676.5003 | 1310.4 | 0.5356% | 0.83079 | Pump | Lowara | potable water | pump | 2 | Electricity | 1.5 | 0 | 0 | 0 | 24 | 0.25 | 7 | 0 | 52 | 8736 | One for back up | 1.5 | 3276 | 40% | 1310.4 | 676.5003 | 2240 | Interior
Exterior
Cost (USD) | Payback (year) | IRR (%) | NPV (USD)
2240 | 3.3112 | 30.04% | 5519.4047 | [23 empty] | Freezer
Heladera
Cámara
Sistema de refrigeración
Refrigeración
Frío de proceso
Pumps and VSD | Cost (USD) | [25 empty] | Frío acond. termico
Pump 1kW | 1000
VSD 1kW | 600 | [25 empty] | Si
Installation | 40% | [25 empty] | No
Lifespan (years) | 20 | [19 empty] | 1.5 |  | 0.4 | 1310.4 | 676.5003 | 2240
Año | USD
0 | -2240
1 | 676.5003
2 | 676.5003
3 | 676.5003
4 | 676.5003
5 | 676.5003
6 | 676.5003
7 | 676.5003
8 | 676.5003
9 | 676.5003
10 | 676.5003
11 | 676.5003
12 | 676.5003
13 | 676.5003
14 | 676.5003
15 | 676.5003
16 | 676.5003
17 | 676.5003
18 | 676.5003
19 | 676.5003
20 | 676.5003

## EEM16
Windows films
Unitary energy cost (USD/kWh) | lifespan (years) | Discount rate | Exchange rate
0.51625 | 15 | 6% | 2
Savings (USD/year) | Energy Savings (kWh/year) | Energy Savings (%) | Emissions avoided (kgCO2/year) | [35 empty] | LISTAS
252.7821 | 489.6461 | 0.2002% | 0.31044
|  |  |  | # | Zone | System | Type | Brand/model | Quantity | Thermal power (BTU/h) | COP | Electric power (kW) | Temperature (ºC) | SP Temperature (ºC) | (hours/day) | Days/week | Weeks/years | % de time on load | Observations | 0 | Pot_inst (kW) | Consumption (kWh/year) | New COP | New thermal power (BTU/h) | Consumption (kWh/year ) | Archeotype | Zone | Zone Surface (m2) | AC consumption (kWh/year) | Sunscreen to add (Yes/No) | Orientation fachada (º) (E-W: 0º / N-S: 90º) | Windows surface (m2) | Heat from windows (%) | Total Heat reduction from film (%) | Savings (kWh/year) | New consumption (kWh/year) | Savings (USD/year) | Cost(USD) |  | Cost (USD/m2)
Cost (USD) | Payback (year) | IRR (%) | NPV (USD) | 1 | Seminar room | AC | Split | Classic | 1 | 7882.0472 | 3.18 | 2.31 | [10 empty] | 0 | 12000 | 3060.288 | 3 | Seminar room |  | 3060.288 | Yes |  | 6 | 25% | 8% | 244.823 | 2815.465 | 126.3911 | 1440 |  | 240 | Yes
3360 | 13.2921 | 0.6996% | -953.2021 | 2 | Seminar room 2 | AC | Split | Classic | 1 | 7882.0472 | 3.18 | 2.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 3060.288 |  | Seminar room 2 |  | 3060.288 | Yes |  | 8 | 25% | 8% | 244.823 | 2815.465 | 126.3911 | 1920 |  |  | No
|  |  |  | 3 | Seminar room 3 | AC | Split | Daikin | 1 | 6858.4047 | 3.21 | 2.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 2662.848 |  | Seminar room 3 |  | 2662.848 |  |  | 0 | 25% | 8% | 0 | 2662.848 | 0 | 0
|  |  |  | 4 | Computer Lab | AC | Split | MDV | 1 | 6994.8904 | 3 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 2715.84 |  | Computer Lab |  | 2715.84 |  |  | 0 | 25% | 8% | 0 | 2715.84 | 0 | 0
|  |  |  | 5 | Computer Lab | AC | Split | Delta | 1 | 7438.4688 | 3.23 | 2.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 2888.064 |  | Computer Lab |  | 2888.064 |  |  | 0 | 25% | 8% | 0 | 2888.064 | 0 | 0
Lifespan (years) | 15 |  |  | 6 | Computer Lab | AC | Split | Westinghouse | 1 | 6448.9477 | 2.79 | 1.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 2503.872 |  | Computer Lab |  | 2503.872 |  |  | 0 | 25% | 8% | 0 | 2503.872 | 0 | 0
Year | USD |  |  | 7 | Lecture Room | AC | Split | Lennox | 1 | 8291.5042 | 2.89 | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 3219.264 |  | Lecture Room |  | 3219.264 |  |  | 0 | 25% | 8% | 0 | 3219.264 | 0 | 0 | Refrigeración
0 | -3360 |  |  | 8 | Lecture Room | AC | Split | Midea | 1 | 8291.5042 | 2.93 | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 3219.264 |  | Lecture Room |  | 3219.264 |  |  | 0 | 25% | 8% | 0 | 3219.264 | 0 | 0 | Frío de proceso
1 | 252.7821 |  |  | 9 | Lecture room Nr2 | AC | Split | Midea | 2 | 8291.5042 | 2.93 | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 6438.528 |  | Lecture room Nr2 |  | 6438.528 |  |  | 0 | 25% | 8% | 0 | 6438.528 | 0 | 0 | Frío acond. termico
2 | 252.7821 |  |  | 10 | Lecture room nNr3 | AC | Split | Daikin | 2 | 6858.4047 | 3.21 | 2.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 5325.696 |  | Lecture room nNr3 |  | 5325.696 |  |  | 0 | 25% | 8% | 0 | 5325.696 | 0 | 0
3 | 252.7821 |  |  | 11 | Lecture room nNr3 | AC | Split | MDV | 1 | 6994.8904 | 3 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 2715.84 |  | Lecture room nNr3 |  | 2715.84 |  |  | 0 | 25% | 8% | 0 | 2715.84 | 0 | 0
4 | 252.7821 |  |  | 12 | Lecture room nNr3 | AC | Split | Streamline | 1 | 9895.2107 | 2.43 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 3841.92 |  | Lecture room nNr3 |  | 3841.92 |  |  | 0 | 25% | 8% | 0 | 3841.92 | 0 | 0
6 | 252.7821 |  |  | 13 | Lecture Room Nr4 | AC | Split | TCL | 3 | 7421.4081 | 3.23 | 2.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8644.32 |  | Lecture Room Nr4 |  | 8644.32 |  |  | 0 | 25% | 8% | 0 | 8644.32 | 0 | 0
7 | 252.7821 |  |  | 14 | Lecture Room Nr4 | AC | Split | Midea | 1 | 8291.5042 | 2.93 | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 3219.264 |  | Lecture Room Nr4 |  | 3219.264 |  |  | 0 | 25% | 8% | 0 | 3219.264 | 0 | 0
8 | 252.7821 |  |  | 15 | Theatre Nr2 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 19297.5753 |  | Theatre Nr2 |  | 19297.5753 |  |  | 0 | 25% | 8% | 0 | 19297.5753 | 0 | 0
9 | 252.7821 |  |  | 16 | Theatre Nr3 (big) | Central AC | Outdoor unit | Trane Oddissey | 2 | 79077.3245 | 3 | 23.1753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84000 | 61405.2116 |  | Theatre Nr3 (big) |  | 61405.2116 |  |  | 0 | 25% | 8% | 0 | 61405.2116 | 0 | 0
10 | 252.7821 |  |  | 17 | Theatre Nr1 | Central AC | Outdoor unit | Carrier | 1 | 49702.642 | 3 | 14.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 19297.5753 |  | Theatre Nr1 |  | 19297.5753 |  |  | 0 | 25% | 8% | 0 | 19297.5753 | 0 | 0
11 | 252.7821 |  |  | 18 | Theatre Nr3 (big) | Central AC | Air handler | Trane Oddissey | 2 | 12710.2276 | 0 | 3.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 9869.76 |  | Theatre Nr3 (big) |  | 9869.76 |  |  | 0 | 25% | 8% | 0 | 9869.76 | 0 | 0
12 | 252.7821 |  |  | 19 | Theatre Nr1 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 |  |  | Theatre Nr1 |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
13 | 252.7821 |  |  | 20 | Theatre Nr2 | Central AC | Air handler | 0 | 1 | 12710.2276 | 0 | 3.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 |  |  | Theatre Nr2 |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
14 | 252.7821 | [25 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
15 | 252.7821 | [25 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[27 empty] | 0% |  | 0 |  |  | 0 | 25% | 8% | 0 | 0 | 0 | 0
[25 empty] | 163385.4181 |  |  | 0 | 163385.4181 | 0 | 0 |  |  |  | 489.6461 | 162895.7721 | 252.7821 | 3360
Note on AU8: [Comentario encadenado] Su versión de Excel le permite leer este comentario encadenado; sin embargo, las ediciones que se apliquen se quitarán si el archivo se abre en una versión más reciente de Excel. Más información: https://go.microsoft.com/fwlink/?linkid=870924 Comentario: Gree livo gen 3

## SUMMARY
| Without cross effects |  |  |  |  | With cross effects
| EEM | Annual savings (USD/year) | Annual energy savings (kWh/year) | Energy savings (% total) | C02 reductions (tonCO2/year) |  | EEM | Annual savings (USD/year) | Annual energy savings (kWh/year) | Energy savings (% total) | C02 reductions (tonCO2/year)
EEM1 | Efficient lighting | #N/A | #N/A | #N/A | #N/A | EEM1 | Efficient lighting | #N/A | #N/A | #N/A | #N/A
EEM2 | Lighting automation | 1063.5521 | 2060.1302 | 0.8421% | 0.0013061 | EEM2 | Lighting automation | 1063.5521 | 2060.1302 | 0.8421% | 0.0013061 | EEM1 -> EEM2
EEM3 | AC automation | 509.5311 | 986.976 | 0.4034% | 0.00062574 | EEM3 | AC automation | 509.5311 | 986.976 | 0.4034% | 0.00062574 | EEM4 -> EEM3
EEM4 | Split AC replacement | 10288.9825 | 19930.048 | 8.147% | 0.012636 | EEM4 | Split AC replacement | 10288.9825 | 19930.048 | 8.147% | 0.012636
RE1 | PV system | 64516.2654 | 286854.0304 | 117.3% | 0.18187 | RE1 | PV system | 64516.2654 | 286854.0304 | 117.3% | 0.18187
| Total | #N/A | #N/A | #N/A | #N/A | 0 | Total | #N/A | #N/A | #N/A | #N/A
| EEM | Investment Cost (USD) | Payback (years) | IRR | NPV (USD) |  | EEM | Investment Cost (USD) | Payback (years) | IRR | NPV (USD)
EEM1 | Efficient lighting | #N/A | #N/A | #VALUE! | #N/A | EEM1 | Efficient lighting | #N/A | #N/A | #VALUE! | #N/A
EEM2 | Lighting automation | 0 | 0 | #NUM! | 7384.7508 | EEM2 | Lighting automation | 0 | 0 | #NUM! | 7384.7508
EEM3 | AC automation | 1883 | 3.6956 | 23.88% | 1761.5029 | EEM3 | AC automation | 1883 | 3.6956 | 23.88% | 1761.5029
EEM4 | Split AC replacement | 15276.36 | 1.4847 | 67.3% | 75810.912 | EEM4 | Split AC replacement | 15276.36 | 1.4847 | 67.3% | 75810.912
RE1 | PV system | 456555 | 7.0766 | 14.51% | 154526.6005 | RE1 | PV system | 456555 | 7.0766 | 14.51% | 154526.6005
| Total | #N/A | #N/A |  |  | 0 | Total | #N/A | #N/A | 0% | 0

## ER1 (hidden)
Datos
Monómico ($/kWh) | Vida útil (años) | Tasa de descuento | Tipo de camnbio |  |  |  | Consumo (lt/mes) |  |  |  | DATOS METEOROLÓGICOS |  |  | CONSUMO |  | CALCULO COLECTORES
18.8472 | 25 | 10% | 2 |  |  |  | Temp de uso (ºC) |  |  | Porcentaje de uso | Taf | Radiación diaria | Tamb | Consumo | Demanda energética | FS | APORTE
[7 empty] | Combustible actual | Electricidad |  | % | ºC | kWh/m2.d | ºC | litros/mes | kWh/mes | % | kWh/mes
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) |  |  |  | Enero | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0!
0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | Área colector (m2) | 1.85 | Febrero | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | Cantidad colectores |  | Marzo | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | Cálculos de rendimiento de colectores |  |  | Cálculos de coeficientes |  |  | Electricidad | 1 | kWh/kWh | 18.8472 | $/kWh | 18.8472 | $/kWh
|  | Vida útil (años) | TIR | VAN |  |  | Superficie máx. para instalar (m2) |  | Abril | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | X | Y | f |  |  |  | Gas Natural | 9.6512 | kWh/m3 | 430 | $/m3 | 44.5542 | $/kWh
|  | 25 | #VALUE! | #DIV/0! |  |  | n0 | 0.73 | Mayo | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Coeficiente global de pérdidas | FrUL (W/m2.K) | 4.779 | Gas oil | 10.093 | kWh/lt | 55.9 | $/lt | 5.5385 | $/kWh
[7 empty] | a1 (W/m2.K) | 3.819 | Junio | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Area de colector | Ac | 0 | GLP | 12.6744 | kWh/kg | 86 | $/kg | 6.7853 | $/kWh
| Energía total Referencia |  | Energía total Medida |  |  |  | a2 (W/m2.K2) | 0.024 | Julio | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Rendimiento | FrUL | 4.779 | Biomasa | 2.3372 | kWh/kg | 4.3 | $/kg | 1.8398 | $/kWh
| 0 | kWh | #DIV/0! | kWh |  |  |  |  | Agosto | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Factor de correción intercambiador | FIC | 1
[7 empty] | Vacumulación (lt) | 300 | Setiembre | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Correción por Vol de ac | CV | #DIV/0!
[7 empty] | Costo unitario (USD/colector) | 500 | Octubre | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Correción por temp de agua cal | CT | 0.116
[7 empty] | Inversión (USD) | 0 | Noviembre | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modificador de ángulo de incidencia | MAI | 0.96
Descripción técnica: | [8 empty] | Diciembre | 100% |  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[18 empty] | #DIV/0! | #DIV/0! | #DIV/0!
[6 empty] | Año | USD |  | Promedio | 1 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total |  |  |  |  | 0 | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[6 empty] | 1 | #DIV/0! | [10 empty] | #DIV/0! | #DIV/0! | #DIV/0!
[6 empty] | 2 | #DIV/0!
[6 empty] | 3 | #DIV/0!
[6 empty] | 4 | #DIV/0!
[6 empty] | 5 | #DIV/0!
Recomendaciones técnicas: | [5 empty] | 6 | #DIV/0!
[6 empty] | 7 | #DIV/0!
[6 empty] | 8 | #DIV/0!
[6 empty] | 9 | #DIV/0!
[6 empty] | 10 | #DIV/0!
[6 empty] | 11 | #DIV/0!
[6 empty] | 12 | #DIV/0!
[6 empty] | 13 | #DIV/0!
[6 empty] | 14 | #DIV/0!
[6 empty] | 15 | #DIV/0!
Note on U7: Federico González Madina: Calculo con la metodología f-chart, detallada en "Manual técnico de energía solar térmica volumen 2"
Note on Y12: Federico González Madina: Este factorr es considerado 1 para facilitar los cálculos y el diseño. No suele variar mucho

## ER2 (hidden)
Datos
Monómico ($/kWh) | Vida útil (años) | Tasa de descuento | Tipo de camnbio | [8 empty] | CALCULO PANELES
0 | #REF! | 10% | 2 | [7 empty] | Consumo energético | APORTE | FS
[11 empty] | kWh/mes | kWh/mes | %
Inversión (USD) | Ahorro energético (kWh/año) | Ahorro (USD/año) | Ahorro energético (%) | Emisiones evitadas (kgCO2/año) | Payback (años) |  | Potencia (kWp) |  | Enero | 31 |  |  | #DIV/0!
0 | 0 | 0 | 0% | 0 | #DIV/0! |  |  |  | Febrero | 28 |  |  | #DIV/0!
[7 empty] | Eficiencia | 12% | Marzo | 31 |  |  | #DIV/0! | Electricidad | 1 | kWh/kWh | 18.8472 | $/kWh | 18.8472 | $/kWh
|  | Vida útil (años) | TIR | VAN |  |  |  |  | Abril | 30 |  |  | #DIV/0! | Gas Natural | 9.6512 | kWh/m3 | 430 | $/m3 | 44.5542 | $/kWh
|  | #REF! | #NUM! | 0 |  |  | Área paneles (m2) | 0 | Mayo | 31 |  |  | #DIV/0! | Gas oil | 10.093 | kWh/lt | 55.9 | $/lt | 5.5385 | $/kWh
[9 empty] | Junio | 30 |  |  | #DIV/0! | GLP | 12.6744 | kWh/kg | 86 | $/kg | 6.7853 | $/kWh
[9 empty] | Julio | 31 |  |  | #DIV/0! | Biomasa | 2.3372 | kWh/kg | 4.3 | $/kg | 1.8398 | $/kWh
| Energía total Referencia |  | Energía total Medida | [5 empty] | Agosto | 31 |  |  | #DIV/0!
| 0 | kWh | 0 | kWh |  |  |  |  | Setiembre | 30 |  |  | #DIV/0!
[7 empty] | Costo unitario (USD/kWp) | 1709 | Octubre | 31 |  |  | #DIV/0!
[7 empty] | Inversión (USD) | 0 | Noviembre | 30 |  |  | #DIV/0!
Descripción técnica: | [8 empty] | Diciembre | 31 |  |  | #DIV/0!
[5 empty] | Año | USD |  |  | Promedio |  | #DIV/0! | #DIV/0! | #DIV/0!
[5 empty] | 0 | 0 |  |  | Total |  | 0 | 0
[5 empty] | 1 | 0
[5 empty] | 2 | 0
[5 empty] | 3 | 0
[5 empty] | 4 | 0
[5 empty] | 5 | 0
Recomendaciones técnicas: |  |  |  |  | 6 | 0
[5 empty] | 7 | 0
[5 empty] | 8 | 0
[5 empty] | 9 | 0
[5 empty] | 10 | 0
[5 empty] | 11 | 0
[5 empty] | 12 | 0
[5 empty] | 13 | 0
[5 empty] | 14 | 0
[5 empty] | 15 | 0
[5 empty] | 16 | 0
[5 empty] | 17 | 0
[5 empty] | 18 | 0
[5 empty] | 19 | 0
[5 empty] | 20 | 0

## Resumen (hidden)
Ranking de medidas
[9 empty] | Medida | Inversión (USD) | Ahorro (USD) | Dificultad de inversión
Nro. | Medida | Inversión (USD) | Ahorro (USD/año) | Ahorro energético (%) | Reducción emisones C02 (kgCO2/año) | Período de repago (años) | Ahorro energía eléctrica (kWh) |  | Ponderación | 33% | 33% | 33% | Puntaje
MMEE1 | Iluminación eficiente | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | MMEE1 | #N/A | #N/A |  | #N/A
MMEE2 | Control automático de iluminación | 0 | 1063.5521 | 0.8421% | 1.3061 | 0 | 2060.1302 |  | MMEE2 | #N/A | #N/A |  | #N/A
MMEE3 | Aislación en cañerías y tanques | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | MMEE3 | #N/A | #N/A |  | #N/A
MMEE4 | Aislación en tanques | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | MMEE4 | #N/A | #N/A |  | #N/A
MMEE5 | Aislación de hornos | 0 | 0 | #DIV/0! | 0 | #DIV/0! | 0 |  | MMEE5 | #N/A | #N/A |  | #N/A
MMEE6 | Aislación en cámaras de frío | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | MMEE6 | #N/A | #N/A |  | #N/A
MMEE7 | Reemplazo de motores por más eficientes | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | MMEE7 | #N/A | #N/A |  | #N/A
MMEE8 | Ajustes en combustión | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | MMEE8 | #N/A | #N/A |  | #N/A
MMEE9 | Instalación de VSD en bombas y ventiladores | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | MMEE9 | #N/A | #N/A |  | #N/A
MMEE10 | Reducción de la presión y temperatura en aire comprimido | 0 | 0 | #DIV/0! | 0 | #DIV/0! | 0 |  | MMEE10 | #N/A | #N/A |  | #N/A
MMEE11 | Ejecución de campañas de fuga en aire comprimido | 0 | 0 | #DIV/0! | 0 | #DIV/0! | 0 |  | MMEE11 | #N/A | #N/A |  | #N/A
MMEE12 | VSD en compresor de aire | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | MMEE12 | #N/A | #N/A |  | #N/A
MMEE13 | Reducción de temperatura de evaporación en sistemas de frío | 0 | 1028.0046 | 0.4202% | 2.5249 | 0 | 3982.5475 |  | MMEE13 | #N/A | #N/A |  | #N/A
MMEE14 | Control de splis: corrección de seteo e instalación de sistemas de control centralizado | 1883 | 509.5311 | 0.4034% | 0.62574 | 3.6956 | 986.976 |  | MMEE14 | #N/A | #N/A |  | #N/A
ER1 | Paneles solares térmicos | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | ER1 | #N/A | #N/A |  | #N/A
ER2 | Paneles solares fotovoltaicos | 0 | 0 | 0% | 0 | #DIV/0! | 0 |  | ER2 | #N/A | #N/A |  | #N/A
| Totales | #N/A | #N/A |  | #N/A | #N/A | #N/A
Nro. | Medida | Inversión (USD) | Ahorro (USD/año) | Ahorro energético (%) | Período de repago (años) |  |  |  | Análisis de ranking de medidas:
ACE1 | Corrección de energía reactiva
ACE2 | Ajustes en la contratación del suministro de energía eléctrica
ACE3 | Ajustes en la contratación del suministro de gas
|  | Ahorro (USD/mes) | #N/A
% total
| Inv EE | #N/A | #N/A
| Inv ER | 0 | #N/A
Inv AT
| Total | #N/A
| Emisiones totales (kgCO2/año) | 0
| % reducc/total | #N/A
| Energía de Referencia (kWh/año) | 244638
| Producción | 0 | 0 | 0 | 0
| ID kWh/prod | #DIV/0!
| ID MMEE 1 | #N/A
| ID MMEE 2 | #DIV/0!
| ID MMEE 3 | #DIV/0!
| ID MMEE 4 | #DIV/0!
| ID MMEE 5 | #DIV/0!
| ID MMEE 6 | #DIV/0!
| ID MMEE 7 | #DIV/0!
| ID MMEE 8 | #DIV/0!
| ID MMEE 9 | #REF!
| ID MMEE 10 | #DIV/0!
| ID MMEE 11 | #DIV/0!
| ID MMEE 12 | #REF!
| ID MMEE 13 | #DIV/0!
| ID MMEE 14 | #DIV/0!